BACnet Protocol Implementation Conformance Statement

Date: January 21, 2013

Vendor Name: ABB, Inc. Vendor ID 127

Product Name: HVAC Drive

Product Model Number: ACH550

Applications Software Version:  314C        Firmware Revision:  0511            BACnet Protocol Revision:  7

Product Description:

The ACH550 is a high-performance adjustable frequency drive specifically designed for HVAC applications.  This product supports native BACnet, connecting directly to the MS/TP LAN. MS/TP baud rates are supported up to 76800, as well as master and slave mode functionalities.  Over BACnet, the drive can be fully controlled as a standard adjustable frequency drive. In addition, up to 16 configurable I/O are available over BACnet to the user application.

BACnet Standardized Device Profile (Annex L):

( BACnet Operator Workstation (B-OWS)

( BACnet Advanced Operator Workstation (B-AWS)

( BACnet Operator Display (B-OD)

( BACnet Building Controller (B-BC)

( BACnet Advanced Application Controller (B-AAC)

( BACnet Application Specific Controller (B-ASC)

( BACnet Smart Sensor (B-SS)

( BACnet Smart Actuator (B-SA)

List all BACnet Interoperability Building Blocks Supported (Annex K):

DS-RP-B	Data Sharing-ReadProperty-B

DS-WP-B	Data Sharing-WriteProperty-B

DM-DDB-B	Device Management-DynamicDeviceBinding-B

DM-DOB-B	Device Management-DynamicObjectBinding-B

DM-DCC-B	Device Management-DeviceCommunicationControl-B

DM-RD-B	Device Management-ReinitializeDevice-B

Segmentation Capability:

( Able to transmit segmented messages	Window Size: -

( Able to receive segmented messages	Window Size: -

Standard Object Types Supported:

Object instantiation is static, i.e. objects cannot be created or deleted.

Refer to tables at end of this document for object details.

Data Link Layer Options:

( BACnet IP, (Annex J)

(BACnet IP, (Annex J), Foreign Device

(ISO 8802-3, Ethernet (Clause 7)

( ATA 878.1, 2.5 Mb. ARCNET (Clause 8)

( ATA 878.1, EIA-485 ARCNET (Clause 8), baud rate(s) ____________

( MS/TP master (Clause 9), baud rate(s): 9600, 19200, 38400, 76800

( MS/TP slave (Clause 9), baud rate(s): 9600, 19200, 38400, 76800

( Point-To-Point, EIA 232 (Clause 10), baud rate(s):

( Point-To-Point, modem, (Clause 10), baud rate(s):

( LonTalk, (Clause 11), medium: __________

( BACnet/ZigBee (ANNEX O)

( Other:

Device Address Binding:

Is static device binding supported? (This is currently necessary for two-way communication with MS/TP slaves and certain other devices.) (Yes	( No

Networking Options:

( Router, Clause 6

BACnet/IP to MS/TP

BACnet/ ISO 8802-3, Ethernet to MS/TP

BACnet/IP to BACnet/ ISO 8802-3, Ethernet

BACnet/IP to BACnet/ ISO 8802-3, Ethernet to MS/TP

( Annex H, BACnet Tunneling Router over IP

(  BACnet/IP Broadcast Management Device  (BBMD)

Does the BBMD support registrations by Foreign Devices?	(  Yes	( No

Max BDT (Broadcast Distribution Table)-Entries:		-

Does the BBMD support network address translation?	( Yes	( No

Network Security Options:

( Non-secure Device - is capable of operating without BACnet Network Security

( Secure Device - is capable of using BACnet Network Security (NS-SD BIBB)

( Multiple Application-Specific Keys:

( Supports encryption (NS-ED BIBB)

( Key Server (NS-KS BIBB)

Character Sets Supported:

Indicating support for multiple character sets does not imply that they can all be supported simultaneously.

( ANSI X3.4	( IBM(/Microsoft( DBCS	( ISO 8859-1

( ISO 10646 (UCS-2)	( ISO 10646 (UCS-4)	( JIS X 0208

If this product is a communication gateway, describe the types of non-BACnet equipment/networks(s) that the gateway supports:

_______________________________________________________________________________________________

_______________________________________________________________________________________________

_______________________________________________________________________________________________

# Object/Property Support Matrix

The following table summarizes the Object Types/Properties Supported:

| Property | Object Type |
| --- | --- |
|  | Device | Binary Input | Binary Output | Binary Value | Analog Input | Analog Output | Analog Value |
| Object Identifier | ( | ( | ( | ( | ( | ( | ( |
| Object Name | (* | ( | ( | ( | ( | ( | ( |
| Object Type | ( | ( | ( | ( | ( | ( | ( |
| System Status | ( |  |  |  |  |  |  |
| Vendor Name | ( |  |  |  |  |  |  |
| Vendor Identifier | ( |  |  |  |  |  |  |
| Model Name | ( |  |  |  |  |  |  |
| Firmware Revision | ( |  |  |  |  |  |  |
| Appl Software Revision | ( |  |  |  |  |  |  |
| Protocol Version | ( |  |  |  |  |  |  |
| Protocol Revision | ( |  |  |  |  |  |  |
| Services Supported | ( |  |  |  |  |  |  |
| Object Types Supported | ( |  |  |  |  |  |  |
| Object List | ( |  |  |  |  |  |  |
| Max APDU Length | ( |  |  |  |  |  |  |
| Segmentation Support | ( |  |  |  |  |  |  |
| APDU Timeout | ( |  |  |  |  |  |  |
| Number APDU Retries | ( |  |  |  |  |  |  |
| Max Master | ( |  |  |  |  |  |  |
| Max Info Frames | ( |  |  |  |  |  |  |
| Device Address Binding | ( |  |  |  |  |  |  |
| Database Revision | ( |  |  |  |  |  |  |
| Present Value |  | ( | ( | ( | ( | ( | ( |
| Status Flags |  | ( | ( | ( | ( | ( | ( |
| Event State |  | ( | ( | ( | ( | ( | ( |
| Out-of-Service |  | ( | ( | ( | ( | ( | ( |
| Units |  |  |  |  | ( | ( | ( |
| Priority Array |  |  | ( | ( ** |  | ( | ( ** |
| Relinquish Default |  |  | ( | ( ** |  | ( | ( ** |
| Polarity |  | ( | ( |  |  |  |  |
| Active Text |  | ( | ( | ( |  |  |  |
| Inactive Text |  | ( | ( | ( |  |  |  |

*  Writable up to 50 characters

** For commandable values only

Binary Input Object Instance Summary

The following table summarizes the Binary Input Objects supported:

| Instance ID | Object Name | Description | Active/Inactive Text | Present Value Access Type |
| --- | --- | --- | --- | --- |
| BI0 | RO 1 ACT | Indicates status of Relay Output 1. | ON/OFF | R |
| BI1 | RO 2 ACT | Indicates status of Relay Output 2. | ON/OFF | R |
| BI2 | RO 3 ACT | Indicates status of Relay Output 3. | ON/OFF | R |
| BI3 | RO 4 ACT | Indicates status of Relay Output 4. (requires OREL-01 option ) | ON/OFF | R |
| BI4 | RO 5 ACT | Indicates status of Relay Output 5. (requires OREL-01 option ) | ON/OFF | R |
| BI5 | RO 6 ACT | Indicates status of Relay Output 6. (requires OREL-01 option ) | ON/OFF | R |
| BI6 | DI 1 ACT | Indicates status of Digital Input 1. | ON/OFF | R |
| BI7 | DI 2 ACT | Indicates status of Digital Input 2. | ON/OFF | R |
| BI8 | DI 3 ACT | Indicates status of Digital Input 3. | ON/OFF | R |
| BI9 | DI 4 ACT | Indicates status of Digital Input 4. | ON/OFF | R |
| BI10 | DI 5 ACT | Indicates status of Digital Input 5. | ON/OFF | R |
| BI11 | DI 6 ACT | Indicates status of Digital Input 6. | ON/OFF | R |

NOTE:  For Present Value Access Types, R = Read-only, W = Writeable, C = Commandable.  Commandable values support priority arrays & relinquish defaults.

Binary Output Object Instance Summary

The following table summarizes the Binary Output Objects supported:

| Instance ID | Object Name | Description | Active/Inactive Text | Present Value Access Type |
| --- | --- | --- | --- | --- |
| BO0 | RO1 CMD | Controls output state of Relay 1. | ON/OFF | C |
| BO1 | RO2 CMD | Controls output state of Relay 2. | ON/OFF | C |
| BO2 | RO3 CMD | Controls output state of Relay 3. | ON/OFF | C |
| BO3 | RO4 CMD | Controls output state of Relay 4. (requires OREL-01 option ) | ON/OFF | C |
| BO4 | RO5 CMD | Controls output state of Relay 5. (requires OREL-01 option ) | ON/OFF | C |
| BO5 | RO6 CMD | Controls output state of Relay 6. (requires OREL-01 option ) | ON/OFF | C |

NOTE:  For Present Value Access Types, R = Read-only, W = Writeable, C = Commandable.  Commandable values support priority arrays & relinquish defaults.

Binary Value Object Instance Summary

The following table summarizes the Binary Value Objects supported:

| Instance ID | Object Name | Description | Active/Inactive Text | Present Value Access Type |
| --- | --- | --- | --- | --- |
| BV0 | RUN/STOP ACT | Indicates drive’s run status, regardless of control source. | RUN/STOP | R |
| BV1 | FWD/REV ACT | Indicates rotational direction of the motor, regardless of control source. | REV/FWD | R |
| BV2 | FAULT ACT | Indicates current fault status of drive. | FAULT/OK | R |
| BV3 | EXT 1/2 ACT | Indicates whether External 1 or External 2 is active control source. | EXT2/EXT1 | R |
| BV4 | HAND/AUTO ACT | Indicates whether drive is in Hand or Auto control. | HAND/AUTO | R |
| BV5 | ALARM ACT | Indicates current alarm status of drive. | ALARM/OK | R |
| BV6 | MAINT REQ | Indicates current maintenance status of drive. | MAINT/OK | R |
| BV7 | DRIVE READY | Indicates drive is ready to accept a run command. | READY/NOT READY | R |
| BV8 | AT SETPOINT | Indicates drive has reached its commanded setpoint. | YES/NO | R |
| BV9 | RUN ENA ACT | Indicates status of Run Enable command, regardless of its source. | ENABLE/DISABLE | R |
| BV10 | RUN/STOP CMD | Command to start drive (drive must be configured for BACnet control). | RUN/STOP | C |
| BV11 | FWD/REV CMD | Command to change rotational direction of motor (drive must be configured for BACnet control). | REV/FWD | C |
| BV12 | RUN ENA CMD | Command to assert Run Enable command (drive must be configured for BACnet control). | ENABLE/DISABLE | C |
| BV13 | EXT 1/2 CMD | Commanded to select External 1 or External 2 as active control source (drive must be configured for BACnet control). | EXT2/EXT1 | C |
| BV14 | FAULT RESET | Commanded to reset fault (drive must be configured for BACnet control). | RESET/NO | C |
| BV15 | MBOX READ | Command to read parameter value specified by AV25, MBOX PARAM. The parameter value is returned in AV26, MBOX DATA. | READ/RESET | W |
| BV16 | MBOX WRITE | Commanded to write data value specified by AV26, MBOX DATA, to the parameter value specified by AV25, MBOX PARAM. | WRITE/RESET | W |
| BV17 | LOCK PANEL | Commanded to lock panel and prevent parameter changes. | LOCK/UNLOCK | W |
| BV18 | CTL OVERRIDE CMD | Commands the drive into BACnet Control Override. In this mode, BACnet acquires drive control from its normal source. Note that HAND mode of the panel has priority over BACnet Control Override. | ON/OFF | C |
| BV19 | CTL OVERRIDE ACT | Indicates if drive has been placed in BACnet Control Override by commanding BV18. In this mode, BACnet acquires drive control from its normal source. Note that HAND mode of the panel has priority over BACnet Control Override. | ON/OFF | R |
| BV20 | START ENABLE 1 | Command to assert Start Enable 1 (drive must be configured for BACnet control). | ENABLE/DISABLE | C |
| BV21 | START ENABLE 2 | Command to assert Start Enable 2 (drive must be configured for BACnet control). | ENABLE/DISABLE | C |

NOTE:  For Present Value Access Types, R = Read-only, W = Writeable, C = Commandable.  Commandable values support priority arrays & relinquish defaults.

Analog Input Object Instance Summary

The following table summarizes the Analog Input Objects supported:

| Instance ID | Object Name | Description | Units | Present Value Access Type |
| --- | --- | --- | --- | --- |
| AI0 | ANALOG INPUT 1 | Indicates the input level of Analog Input 1. | Percent | R |
| AI1 | ANALOG INPUT 2 | Indicates the input level of Analog Input 2. | Percent | R |

NOTE:  For Present Value Access Types, R = Read-only, W = Writeable, C = Commandable.  Commandable values support priority arrays & relinquish defaults.

Analog Output Object Instance Summary

The following table summarizes the Analog Output Objects supported:

| Instance ID | Object Name | Description | Units | Present Value Access Type |
| --- | --- | --- | --- | --- |
| AO0 | AO 1 COMMAND | Controls Analog Output 1 (drive must be configured for BACnet control). | Percent | C |
| AO1 | AO 2 COMMAND | Controls Analog Output 2 (drive must be configured for BACnet control). | Percent | C |

NOTE:  For Present Value Access Types, R = Read-only, W = Writeable, C = Commandable.  Commandable values support priority arrays & relinquish defaults.

Analog Value Object Instance Summary

The following table summarizes the Analog Value Objects supported:

| Instance ID | Object Name | Description | Units | Present Value Access Type |
| --- | --- | --- | --- | --- |
| AV0 | OUTPUT SPEED | Motor speed. | RPM | R |
| AV1 | OUTPUT FREQ | Output frequency. | Hertz | R |
| AV2 | DC BUS VOLT | DC bus voltage. | Volts | R |
| AV3 | OUTPUT VOLT | AC output voltage. | Volts | R |
| AV4 | CURRENT | Output current of drive. | Amps | R |
| AV5 | TORQUE | Output torque of motor as a percentage of nominal torque. | Percent | R |
| AV6 | POWER | Output power in kW. | Kilowatts | R |
| AV7 | DRIVE TEMP | Heatsink temperature. | (C | R |
| AV8 | KWH (R) | Drive’s resettable energy usage (reset by writing 0). | kWh | W |
| AV9 | MWH (NR) | Drive’s cumulative energy usage. This value is not resettable. | MWh | R |
| AV10 | PRC PID FBCK | Process PID feedback signal. | Percent | R |
| AV11 | PRC PID DEV | Deviation of Process PID output signal from its setpoint. | Percent | R |
| AV12 | EXT PID FBCK | External PID feedback signal. | Percent | R |
| AV13 | EXT PID DEV | Deviation of External PID output signal from its setpoint. | Percent | R |
| AV14 | RUN TIME (R) | Drive’s resettable run time (reset by writing 0). | Hours | W |
| AV15 | MOTOR TEMP | Motor temperature as setup in Group 35. | (C | R |
| AV16 | INPUT REF 1 | Input Reference 1 (drive must be configured for BACnet control). | Percent | C |
| AV17 | INPUT REF 2 | Input Reference 2 (drive must be configured for BACnet control). | Percent | C |
| AV18 | LAST FLT | Indicates most recent fault in fault log. | None | R |
| AV19 | PREV FLT 1 | Indicates previous fault in fault log. | None | R |
| AV20 | PREV FLT 2 | Indicates oldest fault in fault log. | None | R |
| AV21 | AO 1 ACT | Indicates output level of Analog Output 1. | Milliamps | R |
| AV22 | AO 2 ACT | Indicates output level of Analog Output 2. | Milliamps | R |
| AV23 | ACCEL1 TIME | Sets Ramp1 acceleration time. | Seconds | W |
| AV24 | DECEL1 TIME | Sets Ramp 1 deceleration time. | Seconds | W |
| AV25 | MBOX PARAM | Sets parameter number to be used by mailbox function (see BV15 & BV16). | None | W |
| AV26 | MBOX DATA | Sets (W) or indicates (R) the data value of mailbox function (see BV15 & BV16). | None | W |
| AV27 | EXT PID STPT | Setpoint for the External PID controller (drive must be configured for BACnet control). | Percent | C |

NOTE:  For Present Value Access Types, R = Read-only, W = Writeable, C = Commandable.  Commandable values support priority arrays & relinquish defaults.

Product photo, ACH550