Protocol Implementation Conformance Statement
Date: 02/6/2013__ 
Vendor Name: Schneider Electric 
Product Name: BACnet Lighting Controller_ 
Product Model Number: SERPBC600 _ 
Applications Software Version: 1.00_ Firmware Revision: 1.10_ BACnet Protocol Revision: 6 

Product Description: 
- The SERPBC600 is a controller that allows: 

· Monitoring of 2 inputs (for switches, movement detectors…) 

· Monitoring and the control of 16 outputs for 2 wires lighting relays. 

- The capacity of the SERPBC600 can be increased up to 66 inputs and 64 outputs by connecting extra cards to its RS485 modbus port: 

· SERPBI621 card allows 16 additional inputs; 

· SERPBO631 card allows 16 additional outputs. 

- The SERPBC600 can be monitored and controlled by a BACnet console through BACnet/IP communication (UDP port). 

- The SERPBC600 can be configured through IP communication (IP port) from a specific “Configuration Console” provided with the SERPBC600. 

BACnet Standardized Device Profile (Annex L): 
 BACnet Application Specific Conroller (B-ASC)

List all BACnet Interoperability Building Blocks Supported (Annex K): 
· Data Sharing BIBBs: 
DS-RP-B (Read Property) 

DS-RPM-B (Read Property Multiple) 

DS-WP-B (Write Property) 

DS-WPM-B (Write Property Multiple) 

- Alarm and Event Management BIBBs: None 

- Scheduling BIBBs: None 

- Trending BIBBs: None 

· Device & Network Management BIBBs: 
DM-DDB-B (Receive Who-Is, send I-Am) 

DM-DOB-B (Receive Who-Has, send I-Have) 

DM-DCC-B (Responds to Device Communication Control) 

DM-RD-B (Reinitialize Device) 
Segmentation Capability: None 

Standard Object Types Supported: 

	Object Type 
	Dynamically 

Creatable 
	Dynamically 

Deletable 
	Optional Properties Supported 
	Writable Properties Not Required In Standard 
	Properties Conditionally Writable 
	Proprietary Properties 
	Property Range Description 

	Binary Input 
	No 
	No 
	Description, Reliability 
	Description, 

Reliability (in “Out Of Service” mode) 
	None 
	None 
	Maximum number of characters for strings: 64 

	Binary Output 
	No 
	No 
	Description, Reliability 
	Description, 

Reliability (in “Out Of Service” mode) 
	None 
	None 
	Maximum number of characters for strings: 64 

	Device 
	No 
	No
	Description, Location, 

Profile Name 
	Description, Location
	None 
	None 
	Maximum number of characters for device strings: 64 


