[image: image1.wmf]


August 2011
ComfortPoint Open Manager R100
Protocol Implementation Conformance Statement (PICS)
	Topic:
	BACnet Protocol Implementation Conformance Statement (PICS)

	Date: 
	August 2011

	Version
	1

	Applicable Products
	Honeywell ComfortPoint Open Manager

	Author:
	Damien Weber


Table of Contents

4Honeywell ComfortPoint Open Manager


7Standard Objects and Properties Supported:


7Accumulator Object:


7Analog Input Object:


8Analog Output Object:


8Analog Value Object:


9Averaging Object:


9Binary Input Object:


10Binary Output Object:


10Binary Value Object:


11Calendar Object:


11Command Object:


11Device Object:


12Event Enrollment Object:


12File Object:


12Group Object:


12Life Safety Point Object:


13Life Safety Zone Object:


13Loop Object:


14Multi-State Input Object:


14Multi-State Output Object:


14Multi-State Value Object:


15Notification Class Object:


15Program Object:


15Pulse Converter Object:


16Schedule Object:


16Trend Log Object:




Honeywell ComfortPoint Open Manager
Annex A - Protocol Implementation Conformance Statement

Date: 24 August 2011
Vendor ID: 17
Vendor Name: Honeywell International, Inc. 

Product Name: ComfortPoint Open Manager
Product Model Number: R100
Applications Software Version: 

Firmware Revision: 
BACnet Protocol Revision:1.4
Product Description and Intended Use:

The Honeywell ComfortPoint Open Manager BACnet Workstation.

BACnet Standardized Device Profile (Annex L):

( BACnet Operator Workstation (B-OWS) 

( BACnet Advanced Operator Workstation (B-AWS) 

( BACnet Operator Display (B-OD) 

( BACnet Building Controller (B-BC) 

( BACnet Advanced Application Controller (B-AAC) 

( BACnet Application Specific Controller (B-ASC)

( BACnet Smart Sensor (B-SS)

( BACnet Smart Actuator (B-SA)
BACnet Interoperability Building Blocks Supported (Annex K):
	Data Sharing
	Data Sharing - Read Property-A
	DS-RP-A

	
	Data Sharing - Read Property-B
	DS-RP-B

	
	Data Sharing - Read Property Multiple-A
	DS-RPM-A

	
	Data Sharing - Write Property-A
	DS-WP-A

	
	Data Sharing - Write Property Multiple-A
	DS-WPM-A

	
	Data Sharing - COV-A
	DS-COV-A

	
	Data Sharing - COVP-A
	DS-COVP-A

	
	Data Sharing – View-A
	DS-V-A

	
	Data Sharing – Advanced View – A
	DS-AV-A

	
	Data Sharing – Proprietary View – A
	DS-PV-A

	
	Data Sharing – Modify-A
	DS-M-A

	
	Data Sharing – Advanced Modify – A
	DS-AM-A

	Alarm & Event 

Management
	Alarm and Event - Notification-A 
	AE-N-A

	
	Alarm and Event - ACK-A 
	AE-ACK-A

	
	Alarm and Event - Alarm Summary View-A 
	AE-AS-A

	
	Alarm and Event – Alarm Summary-A
	AE-ASUM-A

	
	Alarm and Event – Alarm and Event-Enrollment Sumary -A
	AE-ESUM-A

	
	Alarm and Event – Information-A
	AE-INFO-A

	
	Alarm and Event – Advanced View and Modify-A
	AE-AVM-A

	
	Alarm and Event – View Notifications-A
	AE-VN-A

	
	Alarm and Event – Advanced View Notifications-A
	AE-AVN-A

	
	Alarm and Event - LifeSafety-A
	AE-LS-A

	Scheduling
	Scheduling – View and Modify-A
	SCHED-VM-A

	
	Scheduling – Advanced View and Modify-A
	SCHED-AVM-A

	
	Scheduling – Weekly Schedule-A
	SCHED-WS-A

	Trending
	Trending-View-A
	T-V-A

	
	Trending – Automated Trend Retrieval-A
	T-ATR-A

	
	Trending – Advanced View and Modify-A
	T-AVM-A

	Device & Network Management
	Device Management - Automatic Device Mapping-A
	DM-ADM-A

	
	Device Management - Dynamic Device Binding-A
	DM-DDB-A

	
	Device Management - Dynamic Device Binding-B
	DM-DDB-B

	
	Device Management - Dynamic Object Binding-A
	DM-DOB-A

	
	Device Management - Dynamic Object Binding-B
	DM-DOB-B

	

	Device Management - Device Communication Control-A
	DM-DCC-A

	
	Device Management – Manual Time Synchronization-A
	DM-MTS-A

	
	Device Management – Object Creation and Deletion-A
	DM-OCD-A

	
	Device Management - Reinitialise Device-A
	DM-RD-A

	
	Device Management - Restart-A
	DM-R-A

	
	Device Management - Backup and Restore-A
	DM-BR-A

	
	Device Management - List Manipulation-A
	DM-LM-A

	
	Device Management - Connection Establishment-A
	NM-CE-A

	
	Device Management - Automated Network Mapping-A
	DM-ANM-A


Segmentation Capability:

Able to transmit segmented messages 
(   yes
(  no
Window Size _16__
Able to receive segmented messages
(   yes
(  no
Window Size _16__
Standard Object Types Supported:

Device Properties:
	Required Properties
	Optional Properties
	Proprietary Properties

	Object_Identifier
	
	

	Object_Name
	
	

	Object_Type
	
	

	System_Status
	
	

	Vendor_Name
	
	

	Vendor_Identifier
	
	

	Model_Name
	
	

	Firmware_Revision
	
	

	Application_Software_Version
	
	

	
	Location
	

	
	Description
	

	
	Protocol_Conformance _Class
	

	Protocol_Version
	
	

	Protocol_Revision
	
	

	Protocol_Services_Supported
	
	

	Protocol_Object_Types_Supported
	
	

	Object_List
	
	

	Max_APDU_Length_Accepted
	
	

	Segmentation_Supported
	
	

	
	Max_Segments_Accepted
	

	
	APDU_Segment_Timeout
	

	APDU_Timeout
	
	

	Number_Of_APDU_Retries
	
	

	Database Revision
	
	

	Device_Address_Binding
	
	


Data Link Layer Options:

(  BACnet IP, (Annex J) 

(  BACnet IP, (Annex J), Foreign Device



(  ISO 8802-3, Ethernet (Clause 7)

( ANSI/ATA 878.1, 2.5 Mb. ARCNET (Clause 8)

( ANSI/ATA 878.1, RS-485 ARCNET (Clause 8), baud rate(s) ____________

( MS/TP master (Clause 9), baud rate(s): 




( MS/TP slave (Clause 9), baud rate(s): 




( Point-To-Point, EIA 232 (Clause 10), baud rate(s):



( Point-To-Point, modem, (Clause 10), baud rate(s): 



( LonTalk, (Clause 11), medium: __________

( Other:

Device Address Binding:

Is static device binding supported? 

(This is currently necessary for two-way communication with MS/TP slaves and certain other devices.)

( Yes
(   No

Networking Options:

( Router, Clause 6 - List all routing configurations, e.g., ARCNET-Ethernet, Ethernet-MS/TP, etc.

( Annex H, BACnet Tunneling Router over IP
(  BACnet/IP Broadcast Management Device  (BBMD) 

Does the BBMD support registrations by Foreign Devices? (  Yes ( No
Character Sets Supported:

Indicating support for multiple character sets does not imply that they can all be supported simultaneously.

(   ANSI X3.4    

( IBM™/Microsoft™ DBCS    

( JIS C 6226    

( ISO 10646 (UCS-4)    

(   ISO 10646 (UCS-2)

(   ISO 8859-1

Additional Information:
The Honeywell ComfortPoint Open Manager BACnet Workstation supports devices which implement either algorithmic or intrinsic alarming methodologies.
Standard Objects and Properties Supported:

Accumulator Object:
	Readable Properties
	Writable Properties

	Object_Identifier
	

	Object_Name
	

	Object_Type
	

	Present_Value
	Present_Value

	Description
	Description

	Device_Type
	Device_Type

	Status_Flags
	

	Event_State
	

	Reliability
	

	Out_Of_Service
	Out_Of_Service

	Scale
	

	Units
	Units

	Prescale
	Prescale

	Max_Pres_Value
	Max_Pres_Value

	Value_Change_Time
	

	Value_Before_Change
	

	Value_Set
	Value_Set

	Logging_Record
	

	Logging_Object
	Logging_Object

	Pulse_Rate
	Pulse_Rate

	High_Limit
	High_Limit

	Low_Limit
	Low_Limit

	Limit_Monitoring_Interval
	Limit_Monitoring_Interval

	Notification_Class
	Notification_Class

	Time_Delay
	Time_Delay

	Limit_Enable 
	Limit_Enable 

	Event_Enable
	Event_Enable

	Acked_Transitions
	

	Notify_Type 
	Notify_Type

	Event_Time_Stamps
	


Analog Input Object:

	Readable Properties
	Writable Properties

	Object_Identifier 
	

	Object_Name
	

	Object_Type
	

	Present_Value
	Present_Value

	Description
	Description

	Device_Type
	Device_Type

	Status_Flags
	

	Event_State
	

	Reliability
	

	Out_Of_Service
	Out_Of_Service

	Update_Interval
	Update_Interval

	Units 
	Units 

	Min_Pres_Value
	Min_Pres_Value

	Max_Pres_Value
	Max_Pres_Value

	Resolution 
	Resolution 

	COV_Increment 
	COV_Increment 

	Time_Delay 
	Time_Delay 

	Notification_Class 
	Notification_Class

	High_Limit 
	High_Limit 

	Low_Limit 
	Low_Limit 

	Deadband 
	Deadband 

	Limit_Enable 
	Limit_Enable 

	Event_Enable 
	Event_Enable 

	Acked_Transitions 
	

	Notify_Type 
	Notify_Type

	Event_Time_Stamps
	


Analog Output Object:

	Readable Properties
	Writable Properties

	Object_Identifier 
	

	Object_Name 
	

	Object_Type 
	

	Present_Value 
	Present_Value

	Description 
	Description

	Device_Type 
	Device_Type

	Status_Flags 
	

	Event_State 
	

	Reliability 
	

	Out_Of_Service 
	Out_Of_Service 

	Units 
	Units 

	Min_Pres_Value 
	Min_Pres_Value 

	Max_Pres_Value 
	Max_Pres_Value 

	Resolution 
	Resolution 

	Priority_Array 
	

	Relinquish_Default 
	Relinquish_Default 

	COV_Increment 
	COV_Increment 

	Time_Delay 
	Time_Delay 

	Notification_Class 
	Notification_Class

	High_Limit 
	High_Limit 

	Low_Limit 
	Low_Limit 

	Deadband 
	Deadband 

	Limit_Enable 
	Limit_Enable 

	Event_Enable 
	Event_Enable 

	Acked_Transitions 
	

	Notify_Type 
	Notify_Type

	Event_Time_Stamps 
	


Analog Value Object:

	Readable Properties
	Writable Properties

	Object_Identifier 
	

	Object_Name 
	

	Object_Type 
	

	Present_Value 
	Present_Value

	Description 
	Description

	Status_Flags 
	

	Event_State 
	

	Reliability 
	

	Out_Of_Service 
	Out_Of_Service 

	Units 
	Units 

	Priority_Array 
	

	Relinquish_Default 
	Relinquish_Default 

	COV_Increment 
	COV_Increment 

	Time_Delay 
	Time_Delay 

	Notification_Class 
	Notification_Class

	High_Limit 
	High_Limit 

	Low_Limit 
	Low_Limit 

	Deadband 
	Deadband 

	Limit_Enable 
	Limit_Enable 

	Event_Enable 
	Event_Enable 

	Acked_Transitions 
	

	Notify_Type 
	Notify_Type

	Event_Time_Stamps
	


Averaging Object:

	Readable Properties
	Writable Properties

	Object_Identifier
	

	Object_Name
	

	Object_Type
	

	Minimum_Value
	

	Minimum_Value_Timestamp
	

	Average_Value
	

	Variance_Value
	Variance_Value

	Maximum_Value
	

	Maximum_Value_Timestamp
	

	Description
	Description

	Attempted_Samples
	Attempted_Samples

	Valid_Samples
	

	Object_Property_Reference
	Object_Property_Reference

	Window_Interval
	Window_Interval

	Window_Samples
	Window_Samples


Binary Input Object:

	Readable Properties
	Writable Properties

	Object_Identifier 
	

	Object_Name 
	

	Object_Type 
	

	Present_Value 
	Present_Value

	Description 
	Description

	Device_Type 
	Device_Type 

	Status_Flags 
	

	Event_State 
	

	Reliability 
	

	Out_Of_Service 
	Out_Of_Service 

	Polarity 
	Polarity 

	Inavtive_Text 
	Inavtive_Text 

	Active_Text 
	Active_Text 

	Change_Of_State_Time 
	

	Change_Of_State_Count 
	Change_Of_State_Count

	Time_Of_State_Count_Reset 
	

	Elapsed_Active_Time 
	

	Time_Of_Active_Time_Reset 
	

	Time_Delay 
	Time_Delay

	Notification_Class 
	Notification_Class 

	Alarm_Value 
	Alarm_Value 

	Event_Enable 
	Event_Enable 

	Acked_Transitions 
	

	Notify_Type 
	Notify_Type

	Event_Time_Stamps 
	


Binary Output Object:

	Readable Properties
	Writable Properties

	Object_Identifier
	

	Object_Name
	

	Object_Type
	

	Present_Value
	Present_Value

	Description
	Description

	Device_Type
	Device_Type

	Status_Flags
	

	Event_State
	

	Reliability
	

	Out_Of_Service
	Out_Of_Service

	Polarity
	Polarity

	Inavtive_Text
	Inavtive_Text

	Active_Text
	Active_Text

	Change_Of_State_Time
	

	Change_Of_State_Count
	Change_Of_State_Count

	Time_Of_State_Count_Reset
	

	Elapsed_Active_Time
	

	Time_Of_Active_Time_Reset
	

	Minimum_Off_Time
	Minimum_Off_Time

	Minimum_On_Time
	Minimum_On_Time

	Priority_Array
	

	Relinquish_Default
	Relinquish_Default

	Time_Delay
	Time_Delay

	Notification_Class
	Notification_Class

	Feedback_Value
	Feedback_Value

	Event_Enable
	Event_Enable

	Acked_Transitions
	

	Notify_Type
	Notify_Type

	Event_Time_Stamps
	


Binary Value Object:

	Readable Properties
	Writable Properties

	Object_Identifier
	

	Object_Name
	

	Object_Type
	

	Present_Value
	Present_Value

	Description
	Description

	Device_Type
	Device_Type

	Status_Flags
	

	Event_State
	

	Reliability
	

	Out_Of_Service
	Out_Of_Service

	Inavtive_Text
	Inavtive_Text

	Active_Text
	Active_Text

	Change_Of_State_Time
	

	Change_Of_State_Count
	Change_Of_State_Count

	Time_Of_State_Count_Reset
	

	Elapsed_Active_Time
	

	Time_Of_Active_Time_Reset
	

	Minimum_Off_Time
	Minimum_Off_Time

	Minimum_On_Time
	Minimum_On_Time

	Priority_Array
	

	Relinquish_Default
	Relinquish_Default

	Time_Delay
	Time_Delay

	Notification_Class
	Notification_Class

	Alarm_Value
	Alarm_Value

	Event_Enable
	Event_Enable

	Acked_Transitions
	

	Notify_Type
	Notify_Type

	Event_Time_Stamps
	


Calendar Object:

	Readable Properties
	Writable Properties

	Object_Identifier
	

	Object_Name
	

	Object_Type
	

	Description
	Description

	Present_Value
	

	Date_List
	Date_List


Command Object:

	Readable Properties
	Writable Properties

	Object_Identifier
	

	Object_Name
	

	Object_Type
	

	Description
	Description

	Present_Value
	Present_Value

	In_Process
	

	All_Writes_Successful
	

	Action
	

	Action_Text
	Action_Text


Device Object:

	Readable Properties
	Writable Properties

	Object_Identifier
	

	Object_Name
	

	Object_Type
	

	System_Status
	

	Vendor_Name
	

	Vendor_Identifier
	

	Model_Name
	

	Firmware_Revision
	

	Application_Software_Version
	

	Location
	Location

	Description
	Description

	Protocol_Version
	

	Protocol_Revision
	

	Protocol_Services_Supported
	

	Protocol_Object_Types_Supported
	

	Configuration_Files
	Configuration_Files

	Active_COV_Subscriptions
	

	Active_VT_Sessions
	

	APDU_Timeout
	APDU_Timeout

	Auto_Slave_Discovery
	Auto_Slave_Discovery

	Backup_Failure_Timeout
	Backup_Failure_Timeout

	Database_Revision
	

	Device_Addres_Binding
	

	Last_Restore_Time
	

	Manual_Slave_Address_Binding
	Manual_Slave_Address_Binding

	Max_Info_Frames
	Max_Info_Frames

	Max_Master
	Max_Master

	Max_Segments_Accepted
	

	Slave_Address_Binding
	Slave_Address_Binding

	Slave_Proxy_Enable
	Slave_Proxy_Enable

	Time_Synchronization_Recipients
	Time_Synchronization_Recipients

	VT_Classes_Supported
	

	Object_List
	

	Max_APDU_Length_Accepted
	

	Segmentation_Supported
	

	Local_Time
	Local_Time

	Local_Date
	Local_Date

	UTC_Offset
	UTC_Offset

	Daylight_Saving_Status
	Daylight_Saving_Status

	APDU_Segment_Timeout
	APDU_Segment_Timeout

	Number_Of_APDU_Retries
	Number_Of_APDU_Retries


Event Enrollment Object:

	Readable Properties
	Writable Properties

	Object_Identifier
	

	Object_Name
	

	Object_Type
	

	Description
	Description

	Event_Type
	Event_Type

	Notify_Type
	Notify_Type

	Object_Property_Reference
	Object_Property_Reference

	Event_Parameters
	Event_Parameters

	Event_State
	

	Event_Enable
	Event_Enable

	Acked_Transitions
	

	Notification_Class
	Notification_Class

	Event_Time_Stamps
	


File Object:

	Readable Properties
	Writable Properties

	Object_Identifier
	

	Object_Name
	

	Object_Type
	

	Description
	Description

	File_Type
	

	File_Size
	File_Size

	Modification_Date
	

	Archive
	Archive

	Read_Only
	

	Record_Count
	Record_Count

	File_Access_Method
	


Group Object:

	Readable Properties
	Writable Properties

	Object_Identifier
	

	Object_Name
	

	Object_Type
	

	Description
	Description

	List_Of_Group_Members
	

	Present_Value
	


Life Safety Point Object:

	Readable Properties
	Writable Properties

	Object_Identifier
	

	Object_Name
	

	Object_Type
	

	Present_Value
	Present_Value

	Tracking_Value
	

	Description
	

	Device_Type
	

	Status_Flags
	

	Event_State
	

	Reliability
	

	Out_Of_Service
	Out_Of_Service

	Notification_Class
	

	Life_Safety_Alarm_Values
	Life_Safety_Alarm_Values

	Alarm_Values
	Alarm_Values

	Fault_Values
	Fault_Values

	Event_Enable
	Event_Enable

	Acked_Transitions
	

	Notify_Type
	Notify_Type

	Event_Time_Stamps
	

	Silenced
	

	Operation_Expected
	

	Maintenance_Required
	

	Setting
	

	Direct_Reading
	

	Units
	

	Member_Of
	


Life Safety Zone Object:

	Readable Properties
	Writable Properties

	Object_Identifier
	

	Object_Name
	

	Object_Type
	

	Present_Value
	Present_Value

	Tracking_Value
	

	Description
	

	Device_Type
	

	Status_Flags
	

	Event_State
	

	Reliability
	

	Out_Of_Service
	Out_Of_Service

	Notification_Class
	

	Life_Safety_Alarm_Values
	Life_Safety_Alarm_Values

	Alarm_Values
	Alarm_Values

	Fault_Values
	Fault_Values

	Event_Enable
	Event_Enable

	Acked_Transitions
	

	Notify_Type
	Notify_Type

	Event_Time_Stamps
	

	Silenced
	

	Operation_Expected
	

	Maintenance_Required
	

	Zone_Members
	


Loop Object:

	Readable Properties
	Writable Properties

	Object_Identifier
	

	Object_Name
	

	Object_Type
	

	Present_Value
	Present_Value

	Description
	Description

	Status_Flags
	

	Event_State
	

	Reliability
	

	Out_Of_Service
	Out_Of_Service

	Update_Interval
	Update_Interval

	Output_Units
	Output_Units

	Manipulated_Variable_Reference
	Manipulated_Variable_Reference

	Controlled_Variable_Reference
	Controlled_Variable_Reference

	Controlled_Variable_Value
	Controlled_Variable_Value

	Controlled_Variable_Units
	Controlled_Variable_Units

	Setpoint_Reference
	Setpoint_Reference

	Setpoint
	Setpoint

	Action
	Action

	Proportional_Constant
	Proportional_Constant

	Proportional_Constant_Units
	Proportional_Constant_Units

	Integral_Constant
	Integral_Constant

	Integral_Constant_Units
	Integral_Constant_Units

	Derivative_Constant
	Derivative_Constant

	Derivative_Constant_Units
	Derivative_Constant_Units

	Bias
	Bias

	Maximum_Output
	Maximum_Output

	Minimum_Output
	Minimum_Output

	Priority_For_Writing
	Priority_For_Writing

	COV_Increment
	COV_Increment

	Time_Delay
	Time_Delay

	Notification_Class
	Notification_Class

	Error_Limit
	Error_Limit

	Event_Enable
	Event_Enable

	Acked_Transitions
	

	Notify_Type
	Notify_Type

	Event_Time_Stamps
	


Multi-State Input Object:

	Readable Properties
	Writable Properties

	Object_Identifier
	

	Object_Name
	

	Object_Type
	

	Present_Value
	Present_Value

	Description
	Description

	Device_Type
	Device_Type

	Status_Flags
	

	Event_State
	

	Reliability
	

	Out_Of_Service
	Out_Of_Service

	Number_Of_States
	Number_Of_States

	State_Text
	State_Text

	Time_Delay
	Time_Delay

	Notification_Class
	Notification_Class

	Alarm_Values
	Alarm_Values

	Fault_Values
	Fault_Values

	Event_Enable
	Event_Enable

	Acked_Transitions
	

	Notify_Type
	Notify_Type

	Event_Time_Stamps
	


Multi-State Output Object:

	Readable Properties
	Writable Properties

	Object_Identifier
	

	Object_Name
	

	Object_Type
	

	Present_Value
	Present_Value

	Description
	Description

	Device_Type
	Device_Type

	Status_Flags
	

	Event_State
	

	Reliability
	

	Out_Of_Service
	Out_Of_Service

	Number_Of_States
	Number_Of_States

	State_Text
	State_Text

	Priority_Array
	

	Relinquish_Default
	Relinquish_Default

	Time_Delay
	Time_Delay

	Notification_Class
	Notification_Class

	Feedback_Values
	Feedback_Values

	Event_Enable
	Event_Enable

	Acked_Transitions
	

	Notify_Type
	Notify_Type

	Event_Time_Stamps
	


Multi-State Value Object:

	Readable Properties
	Writable Properties

	Object_Identifier
	

	Object_Name
	

	Object_Type
	

	Present_Value
	Present_Value

	Description
	Description

	Status_Flags
	

	Event_State
	

	Reliability
	

	Out_Of_Service
	Out_Of_Service

	Number_Of_States
	Number_Of_States

	State_Text
	State_Text

	Priority_Array
	

	Relinquish_Default
	Relinquish_Default

	Time_Delay
	Time_Delay

	Notification_Class
	Notification_Class

	Alarm_Values
	Alarm_Values

	Fault_Values
	Fault_Values

	Event_Enable
	Event_Enable

	Acked_Transitions
	

	Notify_Type
	Notify_Type

	Event_Time_Stamps
	


Notification Class Object:

	Readable Properties
	Writable Properties

	Object_Identifier
	

	Object_Name
	

	Object_Type
	

	Description
	Description

	Notification_Class
	Notification_Class

	Priority
	Priority

	Recipient_List
	Recipient_List

	Ack_Required
	Ack_Required


Program Object:

	Readable Properties
	Writable Properties

	Object_Identifier
	

	Object_Name
	

	Object_Type
	

	Program_State
	

	Program_Change
	Program_Change

	Reason_For_Halt
	Reason_For_Halt

	Description_Of_Halt
	Description_Of_Halt

	Program_Location
	Program_Location

	Description
	Description

	Instance_Of
	Instance_Of

	Status_Flags
	

	Reliability
	

	Out_Of_Service
	Out_Of_Service


Pulse Converter Object:

	Readable Properties
	Writable Properties

	Object_Identifier
	

	Object_Name
	

	Object_Type
	

	Description
	Description

	Present_Value
	Present_Value

	Input_Reference
	Input_Reference

	Status_Flags
	

	Event_State
	

	Reliability
	

	Out_Of_Service
	Out_Of_Service

	Units
	Units

	Scale_Factor
	Scale_Factor

	Adjust_Value
	Adjust_Value

	Count
	

	Update_Time
	

	Count_Change_Time
	

	Count_Before_Change
	

	COV_Increment
	COV_Increment

	COV_Period
	COV_Period

	Notification_Class
	Notification_Class

	Time_Delay
	Time_Delay

	High_Limit
	High_Limit

	Low_Limit
	Low_Limit

	Deadband
	Deadband

	Limit_Enable
	Limit_Enable

	Event_Enable
	Event_Enable

	Acked_Transitions
	

	Notify_Type
	Notify_Type

	Event_Time_Stamps
	


Schedule Object:

	Readable Properties
	Writable Properties

	Object_Identifier
	

	Object_Name
	

	Object_Type
	

	Present_Value
	

	Description
	Description

	Effective_Period
	Effective_Period

	Weekly_Schedule
	Weekly_Schedule

	Exception_Schedule
	Exception_Schedule

	List_Of_Object_Property_References
	List_Of_Object_Property_References

	Priority_For_Writing
	Priority_For_Writing

	Status_Flags
	

	Reliability
	

	Out_Of_Service
	Out_Of_Service

	Schedule_Default
	Schedule_Default


Trend Log Object:

	Readable Properties
	Writable Properties

	Object_Identifier
	

	Object_Name
	

	Object_Type
	

	Description
	Description

	Log_Enable
	Log_Enable

	Start_Time
	Start_Time

	Stop_Time
	Stop_Time

	Log_DeviceObjectProperty
	Log_DeviceObjectProperty

	Log_Interval
	Log_Interval

	COV_Resubscription_Interval
	COV_Resubscription_Interval

	Client_COV_Increment
	Client_COV_Increment

	Stop_When_Full
	Stop_When_Full

	Buffer_Size
	Buffer_Size

	Log_Buffer
	

	Record_Count
	Record_Count

	Total_Record_Count
	

	Notification_Threshold
	Notification_Threshold

	Records_Since_Notification
	

	Last_Notify_Record
	

	Event_State
	

	Notification_Class
	Notification_Class

	Event_Enable
	Event_Enable

	Acked_Transitions
	

	Notify_Type
	Notify_Type

	Event_Time_Stamps
	






































This document contains Honeywell proprietary information. Information contained herein is to be used solely for the purpose submitted, and no part of this document or its contents shall be reproduced, published, or disclosed to a third party without the express permission of Honeywell International Sàrl.

Honeywell disclaims the implied warranties of merchantability and fitness for a purpose and makes no express warranties except as may be stated in its written agreement with and for its customer.

In no event is Honeywell liable to anyone for any direct, special, or consequential damages. The information and specification in this document are subject to change without notice.

8
www.honeywell.com

www.honeywell.com
7

