[image: image2.png]KIVIC

CONTROL S




BTL Product Testing and Listing Program Application Form


Protocol Implementation Conformance Statement (Normative) 

BACnet Protocol Implementation Conformance Statement

TC-BAC, TC-STUDIO, TC-BACUNL
TotalControl BACnet Advanced Workstation

[image: image3.png]nsed for Temporary Use Only).

Ele Edt Vew Acon Todks tep
E-4-d@3 O@s bR
St Explorer L o x
o) @ : Chiler -
= £ Smalivill
gAn;v:vwahanDema relNla@m S/ bV S RESODAA g ] 1
2 Wicrsoft Sans Se - 10 cA-U- B/ U B---- -\ -\-/#®-0-w-0-8-0-
3 Dave et (Version
e [E _chillrs (Version 2)
g Hoing B = i s
- BirCocled ] Carier Chiler  Generic Chiller McQuay
Chiler Chilr
= = 8k
Toane Chiler Tubo Chiler York Chiler
7 Chillers ( Version 2)
% Boilers ( Version 2 )
3 Actuator [ Version 2 )
Librares 2
[EFPropeties
& Data
Network Manager ax Liininto
2 ] Name Chillers_Version_2
RS Tt Chilles { Version 2 )
Trend Service (20 &l
TechPubskMD 25)
3. LenController (26)
(@ 1] Middle School
13 21 Highschool
1§ [M2A1] South AHU ;':'" _—
1§ oo e i name of he fbra,
1 Annual Schedules ‘Whole Page v .
1 Inputs. Ready
& NetSersor Tatl Output Window vax
2 Dutputs
D tomtllrs [ Erors | [ warnings | [@ messages
2 Progams = Time Descrption Comporent

25 Furiime Logs
2 Sysem Broup
5 TrendLogs

25 Variaes

1 Weekly Schedule
1§ M2k

A M2A51 Yark Fumace ¥
< i) >

873 | 3/16/2009 100401 AM

furkname_1 [1212] has gone offne.

Network Manager

74| 3/16/2009 100401 AM

furkname_1 [1212] has gone offne.

Network Manager

75 | 3/16/2009 100401 AM

furkname_1 [1212] has gone offne.

Network Manager

76 | 3/16/2009 100435 AM

furkname_1 [1212] has gone offne.

Network Manager

77| 3/16/2009 100435 AM

furkname_1 [1212] has gone offne.

Network Manager

RREEEE

78| 3/16/2009 100435 AM

furkname_1 [1212] has gone offne.

Network Manager

Ready





BACnet Protocol Implementation Conformance Statement

(BACnet Testing Laboratories Version) 

Date:  30 April 2012
Vendor Name: 
KMC Controls
Product Name:   Total Control Design Studio Software Suite

Product Model Number:     TC-BAC, TC-BACUNL, TC-STUDIO
Applications Software Version:   3.3.0                                                                    
BACnet Protocol Revision:  135-2008
Product Description:

Design Studio is a BACnet Advanced Operator Workstation that provides monitoring and configuration of connected BACnet controllers.

BACnet Standardized Device Profile (Annex L): BACnet Advanced Workstation (B-AWS)
List all BACnet Interoperability Building Blocks supported (see Annex K in BACnet 2008:
	Data Sharing
	Alarm and Event Management
	Scheduling
	Trending
	Device and Network Management

	DS-RP-A

DS-RP-B 

DS-RPM-A 

DS-RPM-B 

DS-WP-A 

DS-WP-B 

DS-WPM-A 

DS-WPM-B 

DS-COV-A 

DS-V-A 

DS-M-A 

DS-AV-A 

DS-AM-A
	AE-N-A 

AE-ACK-A 

AE-ASUM-A 

AE-ESUM-A 

AE-INFO-A 

AE-AS-A 

AE-VM-A 

AE-AVM-A 

AE-VN-A 

AE-AVN-A
	SCHED-VM-A 

SCHED-AVM-A 

SCHED-WS-A
	T-V-A 

T-AVM-A 

T-ATR-A
	DM-DDB-A 

DM-DDB-B 

DM-DOB-B 

DM-DCC-A 

DM-MTS-A 

DM-RD-A 

DM-BR-A 

DM-OCD-A 

DM-ANM-A 

DM-ADM-A


Which of the following device binding methods does the product support?  (check one or more)

( Send Who-Is, receive I-Am (BIBB DM-DDB-A)

( Receive Who-Is, send I-Am (BIBB DM-DDB-B)

( Send Who-Has, receive I-Have (BIBB DM-DOB-A)

( Receive Who-Has, send I-Have (BIBB DM-DOB-B)

( Manual configuration of recipient device's network number and MAC address
( None of the above
Segmentation Capability (check all that apply):

( Able to transmit segmented messages

Window Size       1476
  
( Able to receive segmented messages

Window Size  
1476
  
Standard Object Types Supported in AWS:

	OBJECT
	CREATABLE
	DELETABLE
	OPTIONAL PROPERTIES

	Device
	No
	No
	APDU_Segment_Timeout, Daylight_Savings_Status, Description, Local_Date, Local_Time, Location,  Time_Synchronization_Recipients and UTC_Offset


Standard Object Types Accessible via AWS:

	OBJECT
	OPTIONAL PROPERTIES

	Access Door
	Description, Door Status, Lock Status, Secured Status, Door Members, Door Unlock Delay Time, Door Alarm State, Masked Alarm Values, Maintenance Required, Time Delay, Notification Class, Alarm Values, Fault Values, Event Enable, Acked Transitions, Notify Type, Event Time Stamps, Profile Name.

	Accumulator


	Acked Transitions,  Description, Device Type, Event Enable, Event Time Stamps, High Limit, Limit Enable, Limit Monitoring Interval, Logging Object, Logging Record, Low Limit, Notification Class, Notify Type, Prescale, Profile Name, Pulse Rate, Reliability, Time Delay, Value Before Change, Value Change Time and Value Set

	Analog Input


	Acked Transitions, COV Increment, Deadband, Description, Device Type, Event Enable, Event Time Stamps, High Limit, Limit Enable, Low Limit, Max Pres Value, Min Pres Value, Notification Class, Notify Type, Profile Name, Reliability, Resolution, Time Delay and Update Interval

	Analog Output 


	Acked Transitions, COV Increment, Deadband, Description, Device Type, Event Enable, Event Time Stamps, High Limit, Limit Enable, Low Limit, Max Pres Value, Min Pres Value, Notification Class, Notify Type, Profile Name, Reliability, Resolution and Time Delay

	Analog value


	Acked Transitions, COV Increment, Deadband, Description, Event Enable, Event Time Stamps, High Limit, Limit Enable, Low Limit, Notification Class, Notify Type, Priority Array, Profile Name, Reliability, Relinquish Default, and Time Delay 

	Averaging  
	Minimum Value Timestamp, Maximum Value Timestamp, Variance Value, Description, Profile Name

	Binary Input


	Acked Transitions, Active Text, Alarm Value, Change Of State Count, Change Of State Time, Description, Device Type, Elapsed Active Time, Event Enable, Event Time Stamps, Inactive Text, Notification Class, Notify Type, Profile Name, Reliability, Time Delay, Time Of Active Time Reset and Time Of State Count Reset

	Binary Output


	Acked Transitions, Active Text, Change Of State Count, Change Of State Time, Description, Device Type, Elapsed Active Time, Event Enable, Event Time Stamps, Feedback Value, Inactive Text, Minimum Off Time, Minimum On Time, Notification Class, Notify Type, Profile Name, Reliability, Time Delay, Time Of Active Time Reset and Time Of State Count Reset

	Binary Value


	Acked Transitions, Active Text, Alarm Value, Change Of State Count, Change Of State Time, Description, Elapsed Active Time, Event Enable, Event Time Stamps, Inactive Text, Minimum Off Time, Minimum On Time, Notification Class, Notify Type, Priority Array, Profile Name, Reliability, Relinquish Default, Time Delay, Time Of Active Time Reset and Time Of State Count Reset

	Calendar
	Description and Profile Name

	Device
	Active COV Subscriptions, Active VT Sessions, APDU Segment Timeout, Auto Slave Discovery, Backup Failure Timeout,  Configuration Files, Daylight Savings Status, Description, Last Restore Time, Local Date, Local Time, Location, Manual Slave Address Binding, Max Info Frames, Max Master, Max Segments Accepted, Profile Name, Slave Address Binding, Slave Proxy Enable, Time Synchronization Recipients, UTC Offset and VT Classes Supported, Structured Object List, UTC Time Synchronization Recipients, Restart Notification Recipients, Time of Device Restart, Last Restart Reason, Time Synchronization Interval, Interval Offset, and Align Intervals

	Event Enrollment
	Description and Profile Name

	Event Log
	Description, Reliability, Start Time, Stop Time, Notification Threshold, Records Since Notification, Last Notify Record, Notification Class, Event Enable, Acked Transitions, Notify Type, Event Time Stamps, Profile Name.

	File
	Description, Profile Name and Record Count

	Group
	Description, Profile Name

	Life Safety Point
	Description, Device Type, Time Delay, Notification Class, Life Safety Alarm Values, Alarm Values, Fault Values, Event Enable, Acked Transitions, Notify Type, Event Time Stamps, Maintenance Required, Setting, Direct Reading, Units, Member Of, Profile Name

	Life Safety Zone
	Description, Device Type, Time Delay, Notification Class, Life Safety Alarm Values, Alarm Values, Fault Values, Event Enable, Acked Transitions, Notify Type, Event Time Stamps, Maintenance Required, Member Of, Profile Name

	Load Control
	Description, State Description, Reliability, Full Duty Baseline, Notification Class, Time Delay, Event Enable, Acked Transitions, Notify Type, Event Time Stamps, Profile Name

	Loop


	Acked Transitions, Bias, COV Increment, Derivative Constant, Derivative Constant Units, Description, Error Limit, Event Enable, Event Time Stamps, Integral Constant, Integral Constant Units, Maximum Output, Minimum Output, Notification Class, Notify Type, Profile Name, Proportional Constant, Proportional Constant Units, Reliability, and Time Delay and Update Interval

	Multi-state Input
	Acked Transitions, Alarm Values, Description, Device Type, Event Enable, Event Time Stamps, Fault Values, Notification Class, Notify Type, Profile Name, Reliability, State Text and Time Delay 

	Multi-state Output
	Acked Transitions, Description, Device Type, Event Enable, Event Time Stamps, Feedback Value, Notification Class, Notify Type, Profile Name, Reliability, State Text and Time Delay 

	Multi-state Value
	Acked Transitions, Alarm Values, Description, Event Enable, Event Time Stamps, Fault Values, Notification Class, Notify Type, Priority Array, Profile Name, Reliability, Relinquish Default, State Text and Time Delay 

	Notification
	Description and Profile Name

	Program


	Description, Description Of Halt, Instance Of, Profile Name, Program Location, Reason For Halt and Reliability

	Schedule
	Description, Exception Schedule, Weekly Schedule, Profile Name

	Structured View
	Description, Subordinate Annotations, Profile Name

	Trend
	Acked Transitions, Description, Event Enable, Event Time Stamps, Last Notify Record, Log DeviceObjectProperty, Log Interval, Notification Class, Notification Threshold, Notify Type, Records Since Notification, Start Time, and Stop Time, COV Resubscription Interval, Client COV Increment, Profile Name, Align Intervals, Trigger, Interval Offset, Reliability

	Trend Log Multiple
	Description, Reliability, Start Time, Stop Time, Align Intervals, Interval Offset, Trigger, Notification Threshold, Records Since Notification, Last Notify Record, Notification Class, Event Enable, Acked Transitions, Notify Type, Event Time Stamps, Profile Name


Data Link Layer Options (check all that are supported):

( BACnet IP, (Annex J) 

( BACnet IP, (Annex J), Foreign Device

( ISO 8802-3, Ethernet (Clause 7)

( ANSI/ATA 878.1, 2.5 Mb. ARCNET (Clause 8)
( ANSI/ATA 878.1, RS-485 ARCNET (Clause 8), baud rate(s) ____________

( MS/TP master (Clause 9), baud rate(s):  9600, 19200, 38400, 76800

( MS/TP slave (Clause 9), baud rate(s):  9600, 19200, 38400, 76800

( Point-To-Point, EIA 232 (Clause 10), baud rate(s): _________________

( Point-To-Point, modem, (Clause 10), baud rate(s): _________________

( LonTalk, (Clause 11), medium: _________________________________

( BACnet/Zigbee (Annex O): ____________________________________
( Other: _____________________________________________________

Networking Options (check all that are supported):

( Router, Clause 6 - List all routing configurations, e.g., ARCNET-Ethernet, Ethernet-MS/TP, etc.:

                    _______________________________________________________________________________

( Annex H.3, BACnet Tunneling Router over UDP/IP

( BACnet/IP Broadcast Management Device (BBMD)

Does the BBMD support registrations by Foreign Devices?    ( Yes   ( No

Does the BBMD support network address translation?            ( Yes   ( No
Character Sets Supported (check all that apply):

Indicating support for multiple character sets does not imply that they can all be supported simultaneously.

( ANSI X3.4

( IBM(/Microsoft( DBCS
( ISO 8859-1
( ISO 10646 (UCS-2)
( ISO 10646 (ICS-4)

( JIS C 6226


If this product is a communication gateway, describe the non-BACnet equipment/network(s) that the gateway supports:

__________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________

Include any addition information about the product's BACnet capabilities relevant to interoperability:

____________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________

Network Security Options

( Non-secure Device – is capable of operating without BACnet Network Security







Revision G
5 of 1
Revision G
5 of 5

[image: image1][image: image2.png]