
BACnet Protocol Implementation Conformance Statement

(BACnet Testing Laboratories Version)

Date: August 24, 2010
Vendor Name: Samsung SDS
Product Name: WPC(Wall Pad Controller)
Product Model Number: WPC-100-X, VC-100-X
Applications Software Version: N/A    Firmware Revision: 1.1
BACnet Protocol Revision: Revision 4 (135-2004)
Product Description:

The WPC series controllers are wall pad controllers for heating and cooling equipment. They can be used as networked thermostats or VAV controllers depending on the configuration being loaded into its memory.
List all BACnet Interoperability Building Blocks supported (see Annex K in BACnet 2004):
DS-RP-B, 

DS-RPM-B, 

DS-WP-B, 

DM-DDB-B,

DM-DOB-B,

DM-DCC-B,

Which of the following device binding methods does the product support?  (check one or more)

( Send Who-Is, receive I-Am (BIBB DM-DDB-A)

( Receive Who-Is, send I-Am (BIBB DM-DDB-B)

( Send Who-Has, receive I-Have (BIBB DM-DOB-A)

( Receive Who-Has, send I-Have (BIBB DM-DOB-B)

( Manual configuration of recipient device's network number and MAC address
( None of the above
Standard Object Types Supported:
	Object-Type
	Supp
	Dynamically

Creatable
	Dynamically

Deletable
	Optional Properties

Supported
	Writable Properties

	Analog Input
	Yes
	No
	No
	Bias
	Present_Value(conditional), Out_of_ Service, Bias

	Analog Output
	Yes
	No
	No
	Min_Pres_Value, Max_Pres_Value
	Present_Value, Out_of_Service, Min_Pres_Value, Max_Pres_Value

	Analog Value
	Yes
	No
	No
	Priority_Array, Relinquish_Default
	Present_Value, Out_of_Service,

Relinquish_Default

	Binary Input
	Yes
	No
	No
	Inactive_Text, Active_Text
	Present_Value(conditional), Out_of_Service, Polarity

	Binary Output
	Yes
	No
	No
	Inactive_Text, Active_Text
	Present_Value, Out_of_Service, Polarity, Relinquish_Default

	Binary Value
	Yes
	No
	No
	Inactive_Text, Active_Text, Priority_Array, Relinquish_Default
	Present_Value, Out_of_Service, Relinquish_Default

	Device
	Yes
	No
	No
	Max_Master, Max_Info_Frames
	Object_Identifier, Object_Name, APDU_Timeout, Number_of_APDU_Retires, Max_Master

	Multi-state Value
	Yes
	No
	No
	State Text, Priority_Array, Relinquish_Default
	Present_Value, Out_Of_Service, Relinquish_Default


Range Restrictions:
	Object-Type
	Property
	Range Restriction

	Analog Input
	Bias
	-100.0 ~ 100.0

	Analog Output
	Min_Pres_Value
Max_Pres_Value
Relinquish_Default
	0 ~ 50
51 ~ 100

Min_Pres_Value ~ Max_Pres_Value

	Device Object
	APDU_Timeout
Number_Of_APDU_Retries

Max_Master
	1000 ~ 10000
1 ~ 5

1 ~ 127

	Multi-State-Value Object
	Present_Value
Relinquish_Default
	1 ~ Number_Of_States
1 ~ Number_Of_States


Data Link Layer Options (check all that are supported):

( BACnet IP, (Annex J) 

( Able to register as a Foreign Device

( ISO 8802-3, Ethernet (Clause 7)

( ANSI/ATA 878.1, 2.5 Mb. ARCNET (Clause 8)
( ANSI/ATA 878.1, RS-485 ARCNET (Clause 8), baud rate(s) ____________

( MS/TP master (Clause 9), baud rate(s): 9600, 19200, 38400, 76800
( MS/TP slave (Clause 9), baud rate(s): 



( Point-To-Point, EIA 232 (Clause 10), baud rate(s): _________________

( Point-To-Point, modem, (Clause 10), baud rate(s): _________________

( LonTalk, (Clause 11), medium: _________________
( Other: _____________________________________________________

Networking Options (check all that are supported):

( Router, Clause 6 - List all routing configurations, e.g., ARCNET-Ethernet, Ethernet-MS/TP, etc.:

_______________________________________________________________________________

( Annex H.3, BACnet Tunneling Router over UDP/IP

( BACnet/IP Broadcast Management Device (BBMD)


Does the BBMD support registrations by Foreign Devices?    ( Yes   ( No

( MS/TP Slave Proxy
Segmentation Capability (check all that apply):

( Able to transmit segmented messages

Window Size  1          
( Able to receive segmented messages

Window Size  1
Character Sets Supported (check all that apply):

Indicating support for multiple character sets does not imply that they can all be supported simultaneously.

( ANSI X3.4

( IBM(/Microsoft( DBCS
( ISO 8859-1
( ISO 10646 (UCS-2)
( ISO 10646 (ICS-4)

( JIS C 6226


If this product is a communication gateway, describe the non-BACnet equipment/network(s) that the gateway supports:

__________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________

Include any addition information about the product's BACnet capabilities relevant to interoperability:

____________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________
1

