# TC Compact Series for BACnet Networks

Figure 1.   TC Compact Series Controllers (TC-24 and TC-36 shown).

Description

The TC Compact Series (Programmable Controller–Compact) for BACnet networks is a high-performance Direct Digital Control (DDC) supervisory equipment controller, which is an integral part of the TALON Automation System. The controllers are classified as either a BACnet Building Controller (B-BC) with support for BACnet/IP or BACnet MS/TP protocols, or as a BACnet Advanced Application Controller (B-AAC) with support for BACnet MS/TP protocol.

The TC Compact Series offers integrated I/O based on state-of-the-art TX-I/O™ Technology, which provides superior flexibility of point and signal types, and makes it an optimal solution for Air Handling Unit (AHU) control. The TC Compact operates stand-alone or networked to perform complex control, monitoring, and energy management functions without relying on a higher-level processor.

The TC Compact Series communicates with other field panels or workstations on a peer-to-peer Automation Level Network (ALN), or on the Field Level Network (FLN), and supports the following communication options:

	Native BACnet/IP communications over 10/100 MB Ethernet networks

	Native BACnet MS/TP on RS-485

The TC Compact is available with 16, 24, or 36 point terminations. Selected models in the Compact Series provide the following options:

	Support for FLN devices.

	An extended temperature range for the control of rooftop devices.

	Support for Island Bus, which uses TX-I/O modules to expand the number of point terminations.

Features

	BACnet Testing Laboratories (BTL) certified Classified as BACnet Building Controllers (B-BC) using the BACnet/IP protocol and/or BACnet MS/TP, or BACnet Advanced Application Controllers (B-AAC) using the BACnet MS/TP protocol for specific models.

	DIN rail mounted device with removable terminal blocks simplifies installation and servicing.

	Proven program sequences to match equipment control applications.

	Built-in energy management applications and DDC programs for complete facility management.

	Comprehensive alarm management, historical data trend collection, operator control, and monitoring functions.

	Message control for terminals, printers, pagers, and workstations.

	Highly configurable I/O using Siemens state-of-the-art TX-I/O™ Technology.

	HMI RS-232 port, which provides laptop connectivity for local operation and engineering.

	Extended battery backup of Real Time Clock.

	Persistent database backup and restore within the controller.

	Optional HOA (Hand/Off/Auto) module for swappable and configurable HOA capability.

	Optional extended temperature range for rooftop installation.

	Optional support for MS/TP devices.

	Auto Save and persistent database backup and restore within the controller.

	PXM10T and PXM10S support: Optional LCD Local user interface with HOA (Hand-off-auto) capability and point commanding and monitoring features.

	MS/TP Point Pickup Module (PPM) support: Universal Inputs can be configured for analog or digital input. Input/Output type is configured by writing to BACnet object properties.

	Web Server support: Web-based Graphical User Interface (GUI) compatible with BACnet® networks. Ideal for small or remote facilities to monitor and control the Building Automation System.

The Compact Series

In addition to building and system management functions, the Compact Series includes several styles of controllers that flexibly meet application needs.

TC-16

The TC-16 provides control of 16 points, including 8 software-configurable universal points.

Point count includes: 3 Universal Input (UI), 5 Universal I/O (U), 2 Digital Input (DI), 3 Analog Output (AOV), and 3 Digital Output (DO).

TC-24

The TC-24 provides control of 24 points, including 16 software-configurable universal points.

Point count includes: 3 Universal Input (UI), 9 Universal I/O (U), 4 Super Universal I/O (X), 3 Analog Output (AOV), 5 Digital Output (DO).

TC-24 Unitary Equipment Controller

The TC-24 Unitary Equipment Controller provides control for 24 points including 16 software configurable universal points, with point types as listed in PXC-24 above. The PXC-24 Unitary Equipment Controller is a BACnet MS/TP device that can be configured as a programmable, stand-alone FLN device when an Insight workstation is not present. When an Insight workstation is present, the PXC-24 Unitary Equipment Controller can operate as either an ALN or FLN device.

TC-36

The TC-36 provides control of 36 local points, including 24 software-configurable universal points.

Point count includes: 18 Universal I/O (U), 6 Super Universal I/O (X), 4 Digital Input (DI), and 8 Digital Output (DO).

The TC-36 offers the flexibility of expanding the total point count through a self-forming Island Bus. With the addition of a TX-I/O Power Supply, up to two TX-I/O modules can be supported. For more information, see the TX-I/O Product Range Technical Specification Sheet (149-476T).

Available Options

The following options are available to match the application:

FLN Support

	The TC-16 and TC-24 “F” models with an FLN license support up to 32 MS/TP devices.

	The TC-36 with an FLN license supports up to 96 MS/TP devices.

For more information about FLN support, contact your local Siemens Solution Partner, Authorized TALON Dealer.

TC-24 Unitary Equipment Controller

The TC Unitary Equipment Controller (UEC) is an MS/TP device that can be configured as a programmable, stand-alone FLN device when a TALON View workstation is not present. When a TALON View workstation is present, the UEC can operate as either an ALN or FLN device.

Extended Temperature Operation

TC-24 "R" models support extended temperature operation, allowing for rooftop installations.

Web Server and Web Services

The TC Compact Series supports Web Server and Web Services functionality. The Web Server license provides an HTML Web-based user interface for your TALON Building Automation System. It is an ideal solution for small or remote facilities with field panels on a BACnet/IP Automation Level Network (ALN).

The Web Server is a licensable option on the TC Compact.

The Web Services must be used in conjunction with a Web Server located on a TC Compact, and provides Web access to database information in TC-24 and TC-16 BACnet/IP controllers.

This solution provides the user the following features: HTML based graphics and user interface; command, monitor, alarm, trend and generate reports on BACnet objects within the controller database including supervised FLN device information, schedule BACnet objects within the controller database including supervised FLN devices.

Hardware

The TC Compact Series consists of the following major components:

	Input/Output Points

	Power Supply

	Controller Processor

Input/Output Points

	The TC Compact input/output points perform A/D or D/A conversion, signal processing, point command output, and communication with the controller processor. The terminal blocks are removable for easy termination of field wiring.

	The Universal and Super Universal points leverage TX-I/O™ Technology from Siemens Building Technologies to configure an extensive variety of point types.

	Universal Input (UI) and Universal Input/Output (U) points are software-selectable to be:

–	0-10V input

–	4-20 mA input

–	Digital Input

–	Pulse Accumulator inputs

–	1K Ni RTD @ 32°F (Siemens, Johnson Controls, DIN Standard)

–	1K Pt RTD (375 or 385 alpha) @ 32°F

–	10K NTC Thermistor (Type 2 and Type 3) @ 77°F

–	100K NTC Thermistor (Type 2) @ 77°F

–	0-10V Analog Output (Universal Input/Output (U) points only)

	Super Universal (X) points (TC-24 and TC-36 only) are software-selectable to be:

–	0-10V input

–	4-20 mA input

–	Digital Input

–	Pulse Accumulator inputs

–	1K Ni RTD @ 32°F (Siemens, Johnson Controls, DIN Standard)

–	1K Pt RTD (375 or 385 alpha) @ 32°F

–	10K NTC Thermistor (Type 2 and Type 3) @ 77°F

–	100K NTC Thermistor (Type 2) @ 77°F

–	0-10V Analog Output

–	4-20 mA Analog Output

–	Digital Output (using external relay)

	Dedicated Digital Input (DI) points (TC-16 only) are dry contact status sensing.

	Digital Output (DO) points are 110/220V 4 Amp (resistive) Form C relays; LEDs indicate the status of each point.

	All TC Compact Series models support 0-10 Vdc Analog Output circuits.

	On TC-24 and TC-36 models, the Super Universal points may be defined as either 0-10 Vdc or 4-20 mA Analog Output circuits.

Power Supply

	The 24 volt DC power supply provides regulated power to the input/output points and active sensors. The power supply is internal to the TC Compact housing, eliminating the need for external power supply and simplifying installation and troubleshooting.

	The power supply works with the processor to ensure smooth power up and power down sequences for the equipment controlled by the I/O points, even through brownout conditions.

Controller Processor

	The TC Compact Series includes a microprocessor-based multi-tasking platform for program execution and communications with the I/O points and with other TC Compacts and field panels over the ALN.

	A Human Machine Interface (HMI) port, with a quick-connect phone jack (RJ-45), uses RS-232 protocol to support operator devices (such as a local user interface or simple CRT terminal), and a phone modem for dial-in service capability.

	A USB Device port supports a generic serial interface for an HMI or Tool connection, or used for memory expansion in select models. The USB Device port does not support firmware flash upgrades.

	The program and database information stored in the TC Compact RAM memory is battery-backed. This eliminates the need for time-consuming program and database re-entry in the event of an extended power failure.

	The firmware, which includes the operating system, is stored in non-volatile flash ROM memory; this enables firmware upgrades in the field.

	Brownout protection and power recovery circuitry protect the controller board from power fluctuations.

	LEDs provide instant visual indication of overall operation, network communication, and low battery warning.

Programmable Control with Application Flexibility

The TC Compact Series of high performance controllers provides complete flexibility, which allows the owner to customize each controller with the exact program for the application.

The control program for each TC Compact is customized to exactly match the application. Proven Powers Process Control Language (PPCL), a text-based programming structure like BASIC, provides direct digital control and energy management sequences to precisely control equipment and optimize energy usage.

Global Information Access

The HMI port supports operator devices, such as a local user interface or simple CRT terminal, and a phone modem for dial-in service capability. Devices connected to the operator terminal port gain global information access.

Multiple Operator Access

Multiple operators can access the network simultaneously. Multiple operator access ensures that alarms are reported to an alarm printer while an operator accesses information from a local terminal. When using the BACnet/IP ALN option, multiple operators may also access the controller through concurrent Telnet sessions and/or local operator terminal ports, plus optional Web interface using the Web Server (PXC-36) or Web Services (PXC-16 or PXC-24) option.

Menu Prompted, English Language Operator Interface

The TC Compact includes a simple, yet powerful, menu-driven English Language Operator Interface that provides, among other things:

	Point monitoring and display

	Point commanding

	Historical trend collection and display for multiple points

	Event scheduling

	Program editing and modification via Powers Process Control Language (PPCL)

	Alarm reporting and acknowledgment

	Continual display of dynamic information

Built-in Direct Digital Control Routines

The TC Compact provides stand-alone Direct Digital Control (DDC) to deliver precise HVAC control and comprehensive information about system operation. It receives information from sensors in the building, processes the information, and directly controls the equipment. The following functions are available in the TC Compact:

	Closed Loop Proportional, Integral and Derivative (PID) control.

	Logical sequencing.

	Alarm detection and reporting.

	Reset schedules.

Built-in Energy Management Applications

The following applications are programmed in the TC Compact Series and require simple parameter input for implementation:

	Automatic Daylight Saving Time switchover

	Duty cycling

	Economizer control

	Event scheduling

	Holiday scheduling

	Night setback control

	Peak Demand Limiting (PDL)

	Temperature-compensated duty cycling

	Temporary schedule override

BACnet Compact Series Specifications

| Dimensions (L × W × D) |  |
| --- | --- |
| TC-16 and TC-24 | 10.7" × 5.9" × 2.45" (272 mm × 150 mm × 62 mm) |
| TC-36 | 11.5" × 5.9" × 3.0" (293 mm × 150 mm × 77 mm) |

| Processor, Battery, and Memory |  |
| --- | --- |
| Processor and Clock Speed | TC-16 and TC-24: Freescale MPC852T, 100 MHz TC-36: Freescale MPC885, 133 MHz |
| Memory | TC-16 and TC-24: 24 MB (16 MB SDRAM, 8 MB Flash ROM) TC-36: 80 MB (64 MB SDRAM,16 MB Flash ROM) |

| Battery backup of Synchronous Dynamic (SD) RAM (field replaceable) | TC-16 and TC-24 Non-rooftop Models: 60 days (accumulated) AA (LR6) 1.5 Volt Alkaline (non-rechargeable) TC-36: 28 days (accumulated) AA (LR6) 1.5 Volt Alkaline (non-rechargeable) Rooftop (Extended Temperature) Models: 90 days (accumulated) AA (LR6) 3.6 Volt Lithium (non-rechargeable) |
| --- | --- |
| Battery backup of Real Time Clock | Non-rooftop Models: 10 years Coin cell (BR2032) 3 Volt lithium Rooftop (Extended Temperature) Models: 18 months Coin cell (BR2032) 3 Volt lithium |

| Communication |  |
| --- | --- |
| A/D Resolution (analog in) | 16 bits |
| D/A Resolution (analog out) | 10 bits |

| BACnet/IP Automation Level Network (ALN) | 10Base-T or 100Base-TX compliant |
| --- | --- |
| BACnet MS/TP Automation Level Network (ALN) | RS-485, 9600 bps to 115.2 Kbps |
| BACnet MS/TP Field Level Network (FLN) on selected models, license required | RS-485, 9600 bps to 76.8 Kbps |

| Human-Machine Interface (HMI) | RS-232 compliant, 1200 bps to 115.2 Kbps |
| --- | --- |
| USB Device port (for non-smoke control applications only) | Standard 1.1 and 2.0 USB device port, Type B female connector. |
| USB Host port on selected models (for ancillary smoke control applications only). | Standard 1.1 and 2.0 USB host port, Type A female connector. |

| Electrical |  |  |
| --- | --- | --- |
| Power Requirements | 24 Vac ±20% input @ 50/60 Hz |  |
| Power Consumption (Maximum) |  | TC-16: 18 VA @ 24 Vac |
|  | TC-24: 20 VA @ 24 Vac |  |
|  | TC-36: 35 VA @ 24 Vac |  |
| AC Power and Digital Outputs | NEC Class 1 Power Limited |  |
| Communication and all other I/O | NEC Class 2 |  |
| Digital Input | Contact Closure Sensing Dry Contact/Potential Free inputs only Does not support counter inputs |  |
| Digital Output | Class 1 Relay |  |
| Analog Output | 0 to 10 Vdc |  |
| Universal Input (UI) and Universal Input/Output (U) | Analog Input Voltage (0-10 Vdc) Current (4-20 mA) 1K Ni RTD @ 32°F 1K Pt RTD (375 or 385 alpha) @ 32°F 10K NTC Type 2 or Type 3 Thermistor @ 77°F 100K NTC Type 2 Thermistor @ 77°F Digital Input Pulse Accumulator Contact Closure Sensing Dry Contact/Potential Free inputs only Supports counter inputs up to 20 Hz Analog Output (Universal Input/Output (U) points only) Voltage (0-10 Vdc) |  |
| Super Universal (X) | Analog Input Voltage (0-10 Vdc) Current (4-20 mA) 1K Ni RTD @ 32°F 1K Pt RTD (375 or 385 alpha) @ 32°F 10K NTC Type 2 or Type 3 Thermistor @ 77°F 100K NTC Type 2 Thermistor @ 77°F Digital Input Pulse Accumulator Contact Closure Sensing Dry Contact/Potential Free inputs only Supports counter inputs up to 20 Hz Analog Output Voltage (0-10 Vdc) Current (4-20 mA) Digital Output (requires an external relay) 0 to 24 Vdc, 22 mA max. |  |

| Operating Environment |  |
| --- | --- |
| Ambient operating temperature | 32°F to 122°F (0°C to 50°C) |
| Ambient operating temperature with rooftop (extended temperature) option | -40°F to 158°F (-40°C to 70°C) |
| Relative Humidity | TC-16 and TC-24: 5% to 95%, non-condensing TC-36: 5% to 93%, non-condensing |
| Mounting Surface | TC-16 and TC-24: Direct equipment mount, building wall, or structural member TC-36: Building wall or a secure structure |

|  | BACnet Testing Laboratories (BTL) Certified, Firmware Revision 3.0 and later |
| --- | --- |

Ordering Information

TC Compact Series

| Part Number | Description |
| --- | --- |
| TC16.2-M.T | TC Compact, 16 point, MS/TP ALN |
| TC16.2-EF.T | TC Compact, 16 point, BACnet/IP ALN, MS/TP FLN |
| TC24.2-M.T | TC Compact, 24 point, MS/TP ALN |
| TC24.2-MR.T | TC Compact, 24 point, MS/TP ALN, rooftop |
| TC24.2-EF.T | TC Compact, 24 point, BACnet/IP ALN, MS/TP FLN option |
| TC24.2-ERF.T | TC Compact, 24 point, BACnet/IP ALN, rooftop, MS/TP FLN option |
| TC36-E.T | TC Compact, 36 point, BACnet/IP or MS/TP ALN |
| TC36-EF.T | TC Compact, 36 point, BACnet/IP or MS/TP ALN, Island Bus support, MS/TP FLN |

Optional Licenses

| Product Number | Description |
| --- | --- |
| LSM-FLN.T | License to enable FLN support on TC-16 or TC-24 "F" models |
| LSM-36.T | License to enable 2 TX-I/O modules on the Island Bus and FLN support on model TC36-E.T |
| LSM-FPEB | License to enable BACnet Web Server (PXC-36) or Web Services (PXC-16/24) |

Accessories

| Product Number | Description |
| --- | --- |
| PXA8-M | 8-switch HOA (UL864) |
| PXA16-M | 16-switch HOA (UL864) |
| PXA16-MR | 16-switch HOA (extended temp, UL 916) with HMI cable |
| PXA-HMI.CABLEP5 | Serial cable required for HOA connection to non-rooftop variants of the 16-point and 24-point Compact Series (pack of 5) |
| TXA1.LLT-P100 | Labels for HOA and TX-I/O Modules, pack of 100, letter format |

Service Boxes and Enclosures

| Product Number | Description |
| --- | --- |
| PXA-SB115V192VA | PX Series Service Box—115V, 24 Vac, 50/60 Hz, 192 VA |
| PXA-SB115V384VA | PX Series Service Box—115V, 24 Vac, 50/60 Hz, 384 VA |
| PXA-SB230V192VA | PX Series Service Box—230V, 24 Vac, 50/60 Hz, 192 VA |
| PXA-SB230V384VA | PX Series Service Box—230V, 24 Vac, 50/60 Hz, 384 VA |
| PXA-ENC18 | 18" Enclosure (Utility Cabinet) (UL Listed NEMA Type 1 Enclosure) |
| PXA-ENC19 | 19” Enclosure (UL Listed NEMA Type 1 Enclosure) |
| PXA-ENC34 | 34” Enclosure (UL Listed NEMA Type 1 Enclosure) |

Documentation

| Product Number | Description |
| --- | --- |
| 588-682 | TC Compact Series Owner's Manual |
| 588-583 | TALON Powers Process Control Language (PPCL) User's Manual |

Compact Series BACnet Protocol Implementation Conformance Statement

Products

| Product | Model Number | Protocol Revision | Software Revsion | Firmware Revision |
| --- | --- | --- | --- | --- |
| BACnet TC Compact Series | TC16.2-EF.T TC16.2-M.T TC24.2-EF.T TC24.2-ERF.T TC24.2-M.T TC24.2-MR.T TC24.2-UCM.T TC36-E.T TC36-EF.T | 135-2004 | N/A | 3.2.2 |

Vendor Information

Siemens Industry, Inc. Building Technologies Division 1000 Deerfield Parkway Buffalo Grove, IL 60089 www.buildingtechnologies.siemens.com/bt/us

Product Description

An integral member of the TALON product family, the TC Compact for BACnet Networks is a high performance, modular Direct Digital Control (DDC) supervisory equipment and primary building controller. The TC Compact operates stand-alone or networked to perform complex control, monitoring and energy management functions without relying on a higher-level processor. The TC Compact communicates on a 10/100 MB Ethernet BACnet/IP or BACnet MS/TP network and optionally supervises BACnet MS/TP devices.

BACnet Standardized Device Profile (Annex L)

| Supported | Device Profile |
| --- | --- |
|  | BACnet Operator Workstation (B-OWS) |
| • | BACnet Building Controller (B-BC) |
|  | BACnet Advanced Application Controller (B-AAC) |
|  | BACnet Application Specific Controller (B-ASC) |
|  | BACnet Smart Actuator (B-SA) |
|  | BACnet Smart Sensor (B-SS) |

Supported BACnet Interoperability Building Block (BIBBs)

| BIBB | Name | Initiate | Execute |
| --- | --- | --- | --- |
| Data Sharing |  |  |  |
| DS-RP-A | Data Sharing-ReadProperty-A | • |  |
| DS-RP-B | Data Sharing-ReadProperty-B |  | • |
| DS-RPM-A | Data Sharing-ReadPropertyMultiple-A | • |  |
| DS-RPM-B | Data Sharing-ReadPropertyMultiple-B |  | • |
| DS-WP-A | Data Sharing-WriteProperty-A | • |  |
| DS-WP-B | Data Sharing-WriteProperty-B |  | • |
| DS-WPM-B | Data Sharing-WritePropertyMultiple-B |  | • |
| DS-COV-A | Data Sharing-COV-A | • |  |
| DS-COV-B | Data Sharing-COV-B |  | • |
| DS-COVU-A | Data Sharing-COV-Unsolicited-A | • |  |
| DS-COVU-B | Data Sharing-COV-Unsolicited-B |  | • |

| Scheduling |  |  |  |
| --- | --- | --- | --- |
| SCHED-I-B | Scheduling-Internal-B |  | • |
| SCHED-E-B | Scheduling-External-B |  | • |

| Alarm and Event Management |  |  |  |
| --- | --- | --- | --- |
| AE-N-A | Alarm and Event-Notification-A | • |  |
| AE-N-I-B | Alarm and Event-Notification Internal-B |  | • |
| AE-N-E-B | Alarm and Event-Notification External-B |  | • |
| AE-ACK-A | Alarm and Event-ACK-A | • |  |
| AE-ACK-B | Alarm and Event-ACK-B |  | • |
| AE-ASUM-B | Alarm and Event-Alarm Summary-B |  | • |
| AE-ESUM-A | Alarm and Event-Enrollment Summary-A | • |  |
| AE-ESUM-B | Alarm and Event-Enrollment Summary-B |  | • |
| AE-INFO-A | Alarm and Event-Information-A | • |  |
| AE-INFO-B | Alarm and Event-Information-B |  | • |

| Trending |  |  |  |
| --- | --- | --- | --- |
| T-VMT-A | Trending-Viewing and Modifying Trends-A | • |  |
| T-VMT-I-B | Trending-Viewing and Modifying Trends-Internal-B |  | • |
| T-VMT-E-B | Trending-Viewing and Modifying Trends-External-B |  | • |
| T-ATR-B | Trending-Automated Trend Retrieval-B |  | • |

| Network Management |  |  |  |
| --- | --- | --- | --- |
| NM-CE-A | Network Management-Connection Establishment-A | • |  |

| Device Management |  |  |  |
| --- | --- | --- | --- |
| DM-DDB-A | Device Management-Dynamic Device Binding-A | • |  |
| DM-DDB-B | Device Management-Dynamic Device Binding-B |  | • |
| DM-DOB-A | Device Management-Dynamic Object Binding-A | • |  |
| DM-DOB-B | Device Management-Dynamic Object Binding-B |  | • |
| DM-DDC-B | Device Management-DeviceCommunicationControl-B |  | • |
| DM-PT-A | Device Management-Private Transfer-A | • |  |
| DM-PT-B | Device Management-Private Transfer-B |  | • |
| DM-TM-A | Device Management-Text Message-A | • |  |
| DM-TM-B | Device Management-Text Message-B |  | • |
| DM-TS-B | Device Management-TimeSynchronization-B |  | • |
| DM-RD-B | Device Management-ReinitializeDevice-B |  | • |
| DM-BR-B | Device Management-Backup and Restore-B |  | • |
| DM-LM-B | Device Management-List Manipulation-B |  | • |
| DM-OCD-B | Device Management-Object Creation and Deletion-B |  | • |

Standard Object Types Supported

| Name | Creatable | Deletable |
| --- | --- | --- |
| Analog Input |  |  |
| Analog Output |  |  |
| Analog Value |  |  |
| Binary Inpute |  |  |
| Binary Output |  |  |
| Binary Value |  |  |
| Calendar | • | • |
| Command | • | • |
| Device |  |  |
| Event Enrollment | • | • |
| File |  |  |
| Multi-state Output |  |  |
| Multi-state Value |  |  |
| Notification Class | • | • |
| Schedule | • | • |
| Trend Log |  |  |

Object Attributes

O indicates that the property is optional, per the BACnet standard.

R indicates that the property is required to be present and readable using BACnet services.

Yes indicates that the property is required to be present, readable, and writable using BACnet services.

| Analog Input Object Type |  |  |  |
| --- | --- | --- | --- |
| Property_Identifier | Supported | Writable | Required \ Optional |
| Object_Identifier | Yes |  | R |
| Object_Name | Yes |  | R |
| Object_Type | Yes |  | R |
| Present_Value | Yes | Yes | R |
| Description | Yes | Yes | O |
| Device_Type | Yes |  | O |
| Status_Flags | Yes |  | R |
| Event_State | Yes |  | R |
| Reliability | Yes |  | O |
| Out_Of_Service | Yes | Yes | R |
| Units | Yes | Yes | R |
| Resolution | Yes |  | O |
| COV_Increment | Yes | Yes | O |
| Time_Delay | Yes - Alarm |  | O |
| Notification Class | Yes - Alarm | Yes | O |
| High_Limit | Yes - Alarm | Yes | O |
| Low_Limit | Yes - Alarm | Yes | O |
| Deadband | Yes - Alarm |  | O |
| Limit_Enable | Yes - Alarm |  | O |
| Event_Enable | Yes - Alarm | Yes | O |
| Acked_Transitions | Yes - Alarm |  | O |
| Notify_Type | Yes - Alarm |  | O |
| Event_Time_Stamps | Yes - Alarm |  | O |
| Analog Output Object Type |  |  |  |
| Property_Identifier | Supported | Writable | Required \ Optional |
| Object_Identifier | Yes |  | R |
| Object_Name | Yes |  | R |
| Object_Type | Yes |  | R |
| Present_Value | Yes | Yes | W |
| Description | Yes | Yes | O |
| Device_Type | Yes |  | O |
| Status_Flags | Yes |  | R |
| Event_State | Yes |  | R |
| Reliability | Yes |  | O |
| Out_Of_Service | Yes |  | R |
| Units | Yes |  | R |
| Min_Pres_Value | No |  | O |
| Max_Pres_Value | No |  | O |
| Resolution | Yes |  | O |
| Priority_Array | Yes |  | R |
| Relinquish_default | Yes |  | R |
| COV_Increment | Yes | Yes | O |
| Time_Delay | Yes - Alarm |  | O |
| Notification Class | Yes - Alarm | Yes | O |
| High_Limit | Yes - Alarm | Yes | O |
| Low_Limit | Yes - Alarm | Yes | O |
| Deadband | Yes - Alarm |  | O |
| Limit_Enable | Yes - Alarm |  | O |
| Event_Enable | Yes - Alarm | Yes | O |
| Acked_Transitions | Yes - Alarm |  | O |
| Notify_Type | Yes - Alarm |  | O |
| Event_Time_Stamps | Yes - Alarm |  | O |
| Analog Value Object Type |  |  |  |
| Property_Identifier | Supported | Writable | Required \ Optional |
| Object_Identifier | Yes |  | R |
| Object_Name | Yes |  | R |
| Object_Type | Yes |  | R |
| Present_Value | Yes | Yes | R |
| Description | Yes | Yes | O |
| Status_Flags | Yes |  | R |
| Event_State | Yes |  | R |
| Reliability | Yes |  | O |
| Out_Of_Service | Yes |  | R |
| Units | Yes |  | R |
| Priority_Array | Yes |  | O |
| Relinquish_default | Yes |  | O |
| COV_Increment | Yes | Yes | O |
| Time_Delay | Yes - Alarm |  | O |
| Notification Class | Yes - Alarm | Yes | O |
| High_Limit | Yes - Alarm | Yes | O |
| Low_Limit | Yes - Alarm | Yes | O |
| Deadband | Yes - Alarm |  | O |
| Limit_Enable | Yes - Alarm |  | O |
| Event_Enable | Yes - Alarm | Yes | O |
| Acked_Transitions | Yes - Alarm |  | O |
| Notify_Type | Yes - Alarm |  | O |
| Event_Time_Stamps | Yes - Alarm |  | O |
| Binary Input Object Type |  |  |  |
| Property_Identifier | Supported | Writable | Required \ Optional |
| Object_Identifier | Yes |  | R |
| Object_Name | Yes |  | R |
| Object_Type | Yes |  | R |
| Present_Value | Yes | Yes | R |
| Description | Yes | Yes | O |
| Device_Type | Yes |  | O |
| Status_Flags | Yes |  | R |
| Event_State | Yes |  | R |
| Reliability | Yes |  | O |
| Out_Of_Service | Yes | Yes | R |
| Polarity | Yes |  | R |
| Inactive_Text | Yes |  | O |
| Active_Text | Yes |  | O |
| Elapsed_Active_Time | Yes | Yes | O |
| Time_Of_Active_Time_Reset | Yes |  | O |
| Time_Delay | Yes - Alarm |  | O |
| Notification Class | Yes - Alarm | Yes | O |
| Alarm_Value | Yes - Alarm |  | O |
| Event_Enable | Yes - Alarm | Yes | O |
| Acked_Transitions | Yes - Alarm |  | O |
| Notify_Type | Yes - Alarm |  | O |
| Event_Time_Stamps | Yes - Alarm |  | O |
| Binary Output Object Type |  |  |  |
| Property_Identifier | Supported | Writable | Required \ Optional |
| Object_Identifier | Yes |  | R |
| Object_Name | Yes |  | R |
| Object_Type | Yes |  | R |
| Present_Value | Yes | Yes | W |
| Description | Yes | Yes | O |
| Device_Type | Yes |  | O |
| Status_Flags | Yes |  | R |
| Event_State | Yes |  | R |
| Reliability | Yes |  | O |
| Out_Of_Service | Yes |  | R |
| Polarity | Yes |  | R |
| Inactive_Text | Yes |  | O |
| Active_Text | Yes |  | O |
| Elapsed_Active_Time | Yes | Yes | O |
| Time_Of_Active_Time_Reset | Yes |  | O |
| Priority_Array | Yes |  | R |
| Relinquish_default | Yes |  | R |
| Time_Delay | Yes - Alarm |  | O |
| Notification Class | Yes - Alarm | Yes | O |
| Feedback_Value | Yes - Alarm |  | O |
| Event_Enable | Yes - Alarm | Yes | O |
| Acked_Transitions | Yes - Alarm |  | O |
| Notify_Type | Yes - Alarm |  | O |
| Event_Time_Stamps | Yes - Alarm |  | O |
| Binary Value Object Type |  |  |  |
| Property_Identifier | Supported | Writable | Required \ Optional |
| Object_Identifier | Yes |  | R |
| Object_Name | Yes |  | R |
| Object_Type | Yes |  | R |
| Present_Value | Yes | Yes | R |
| Description | Yes | Yes | O |
| Status_Flags | Yes |  | R |
| Event_State | Yes |  | R |
| Reliability | Yes |  | O |
| Out_Of_Service | Yes |  | R |
| Inactive_Text | Yes |  | O |
| Active_Text | Yes |  | O |
| Elapsed_Active_Time | Yes | Yes | O |
| Time_Of_Active_Time_Reset | Yes |  | O |
| Priority_Array | Yes |  | O |
| Relinquish_default | Yes |  | O |
| Time_Delay | Yes - Alarm |  | O |
| Notification Class | Yes - Alarm | Yes | O |
| Alarm_Value | Yes - Alarm |  | O |
| Event_Enable | Yes - Alarm | Yes | O |
| Acked_Transitions | Yes - Alarm |  | O |
| Notify_Type | Yes - Alarm |  | O |
| Event_Time_Stamps | Yes - Alarm |  | O |
| Calendar Object Type |  |  |  |
| Property_Identifier | Supported | Writable | Required \ Optional |
| Object_Identifier | Yes |  | R |
| Object_Name | Yes |  | R |
| Object_Type | Yes |  | R |
| Description | Yes | Yes | O |
| Present_Value | Yes |  | R |
| Date_List | Yes | Yes | R |
| Command Object Type |  |  |  |
| Property_Identifier | Supported | Writable | Required \ Optional |
| Object_Identifier | Yes |  | R |
| Object_Name | Yes |  | R |
| Object_Type | Yes |  | R |
| Description | Yes | Yes | O |
| Present_Value | Yes | Yes | W |
| In_Process | Yes |  | R |
| All_Writes_Successful | Yes |  | R |
| Action | Yes | Yes | R |
| Action _Text | Yes | Yes | O |
| Device Object Type |  |  |  |
| Property_Identifier | Supported | Writable | Required \ Optional |
| Object_Identifier | Yes |  | R |
| Object_Name | Yes |  | R |
| Object_Type | Yes |  | R |
| System_Status | Yes |  | R |
| Vendor_Name | Yes |  | R |
| Vendor_Identifier | Yes |  | R |
| Model_Name | Yes |  | R |
| Firmware_Revision | Yes |  | R |
| Application_Software_Version | Yes |  | R |
| Location | Yes |  | O |
| Description | Yes |  | O |
| Protocol_Version | Yes |  | R |
| Protocol_Revision | Yes |  | R |
| Protocol_Services_Supported | Yes |  | R |
| Protocol_Object_Types_Supported | Yes |  | R |
| Object_List | Yes |  | R |
| Max_APDU_Lenght_Accepted | Yes |  | R |
| Segmentation_Supported | Yes |  | R |
| Max_Segments_Supported | Yes |  | O |
| Local_Time | Yes |  | O |
| Local_Date | Yes |  | O |
| Daylight_Savings_Status | Yes |  | O |
| APDU_Segment_Timeout | Yes |  | O |
| APDU_Timeout | Yes |  | R |
| Number_Of_APDU_Retries | Yes |  | R |
| Device_Address_Binding | Yes |  | R |
| Database_Revision | Yes |  | R |
| Configuration_Files | Yes |  | O |
| Last_Restore_Time | Yes |  | O |
| Backup_Failure_Timeout | Yes | Yes | O |
| Active_COV_Subscriptions | Yes |  | O |
| Event Enrollment Object Type |  |  |  |
| Property_Identifier | Supported | Writable | Required \ Optional |
| Object_Identifier | Yes |  | R |
| Object_Name | Yes |  | R |
| Object_Type | Yes |  | R |
| Description | Yes | Yes | O |
| Event_Type | Yes |  | R |
| Notify_Type | Yes | Yes | R |
| Event_Parameters | Yes | Yes | R |
| Object_Property_Ref | Yes |  | R |
| Event_State | Yes |  | R |
| Event_Enable | Yes | Yes | R |
| Acked_Transitions | Yes |  | R |
| Notification Class | Yes | Yes | R |
| Event_Time_Stamps | Yes |  | R |
| File Object Type |  |  |  |
| Property_Identifier | Supported | Writable | Required \ Optional |
| Object_Identifier | Yes |  | R |
| Object_Name | Yes |  | R |
| Object_Type | Yes |  | R |
| Description | Yes |  | O |
| File_Type | Yes |  | R |
| File_Size | Yes | Yes | R |
| Modification_Date | Yes |  | R |
| Archive | Yes | Yes | W |
| Read_only | Yes |  | R |
| File_Access_Method | Yes |  | R |
| Multi-state Output Object Type |  |  |  |
| Property_Identifier | Supported | Writable | Required \ Optional |
| Object_Identifier | Yes |  | R |
| Object_Name | Yes |  | R |
| Object_Type | Yes |  | R |
| Present_Value | Yes | Yes | W |
| Description | Yes | Yes | O |
| Device_Type | Yes |  | O |
| Status_Flags | Yes |  | R |
| Event_State | Yes |  | R |
| Reliability | Yes |  | O |
| Out_Of_Service | Yes | Yes | R |
| Number_Of_States | Yes |  | R |
| State_Text | Yes |  | O |
| Priority_Array | Yes |  | R |
| Relinquish_default | Yes |  | R |
| Time_Delay | Yes - Alarm |  | O |
| Notification Class | Yes - Alarm | Yes | O |
| Feedback_Value | Yes - Alarm |  | O |
| Event_Enable | Yes - Alarm | Yes | O |
| Acked_Transitions | Yes - Alarm |  | O |
| Notify_Type | Yes - Alarm |  | O |
| Event_Time_Stamps | Yes - Alarm |  | O |
| Multi-state Value Object Type |  |  |  |
| Property_Identifier | Supported | Writable | Required \ Optional |
| Object_Identifier | Yes |  | R |
| Object_Name | Yes |  | R |
| Object_Type | Yes |  | R |
| Present_Value | Yes | Yes | R |
| Description | Yes | Yes | O |
| Status_Flags | Yes |  | R |
| Event_State | Yes |  | R |
| Reliability | Yes |  | O |
| Out_Of_Service | Yes | Yes | R |
| Number_Of_States | Yes |  | R |
| State_Text | Yes |  | O |
| Priority_Array | Yes |  | O |
| Relinquish_default | Yes |  | O |
| Time_Delay | Yes - Alarm |  | O |
| Notification Class | Yes - Alarm | Yes | O |
| Alarm_Values | Yes - Alarm |  | O |
| Fault_Values | Yes - Alarm |  | O |
| Event_Enable | Yes - Alarm | Yes | O |
| Acked_Transitions | Yes - Alarm |  | O |
| Notify_Type | Yes - Alarm |  | O |
| Event_Time_Stamps | Yes - Alarm |  | O |
| Notification Class Object Type |  |  |  |
| Property_Identifier | Supported | Writable | Required \ Optional |
| Object_Identifier | Yes |  | R |
| Object_Name | Yes |  | R |
| Object_Type | Yes |  | R |
| Description | Yes | Yes | O |
| Notification_Class | Yes |  | R |
| Priority | Yes | Yes | R |
| Ack_Required | Yes | Yes | R |
| Recipient_List | Yes | Yes | R |
| Schedule Object Type |  |  |  |
| Property_Identifier | Supported | Writable | Required \ Optional |
| Object_Identifier | Yes |  | R |
| Object_Name | Yes |  | R |
| Object_Type | Yes |  | R |
| Present_Value | Yes | Yes | R |
| Description | Yes | Yes | O |
| Effective_Period | Yes | Yes | R |
| Weekly_Schedule | Yes | Yes | O |
| Exception_Schedule | Yes | Yes | O |
| Schedule_Default | Yes | Yes | R |
| List_Of_Object_ Property_References | Yes | Yes | R |
| Priority_For_Writing | Yes | Yes | R |
| Status_Flags | Yes |  | R |
| Reliability | Yes |  | R |
| Out_Of_Service | Yes | Yes | R |
| Trend Log Object Type |  |  |  |
| Property_Identifier | Supported | Writable | Required \ Optional |
| Object_Identifier | Yes |  | R |
| Object_Name | Yes |  | R |
| Object_Type | Yes |  | R |
| Description | Yes | Yes | O |
| Log_Enable | Yes | Yes | W |
| Start_Time | Yes | Yes | O |
| Stop_Time | Yes | Yes | O |
| Log_DeviceObjectProperty | Yes |  | O |
| Log_Interval | Yes |  | O |
| Client_COV_Interval | Yes |  | O |
| Stop_When_Full | Yes | Yes | R |
| Buffer_Size | Yes |  | R |
| Log_Buffer | Yes |  | R |
| Record_Count | Yes | Yes | W |
| Total_Record_Count | Yes |  | R |
| Notification_Threshold | Yes - Alarm | Yes | O |
| Records_Since_Notification | Yes - Alarm |  | O |
| Last_Notify_Record | Yes - Alarm |  | O |
| Event_State | Yes - Alarm |  | R |
| Notification_Class | Yes - Alarm | Yes | O |
| Event_Enable | Yes - Alarm |  | O |
| Acked_Transitions | Yes - Alarm |  | O |
| Notify_Type | Yes - Alarm |  | O |
| Event_Time_Stamps | Yes - Alarm |  | O |

Data Link Layer Options

| • | BACnet IP, (Annex J) |
| --- | --- |
| • | BACnet IP, (Annex J), Foreign Device |
|  | ISO 8802-3, Ethernet (Clause 7) |
|  | ANSI/ATA 878.1, 2.5 Mb. ARCNET (Clause 8) |
|  | ANSI/ATA 878.1, RS-485 ARCNET (Clause 8), baud rate(s) ____________ |
| • | MS/TP master (Clause 9), baud rate(s): 9600 bps, 19200 bps, 38400 bps, 76800 bps |
|  | MS/TP slave (Clause 9), baud rate(s): ____________ |
|  | Point-To-Point, EIA 232 (Clause 10), baud rate(s): _________________ |
|  | Point-To-Point, modem, (Clause 10), baud rate(s): _________________ |
|  | LonTalk, (Clause 11), medium: _________________________________ |
|  | Other: _____________________________________________________ |

Segmentation Capability

| Able to transmit segmented messages | Yes | Window Size: 32 |
| --- | --- | --- |
| Able to recieve segmented messages | Yes | Window Size: 32 |

Device Address Binding

| Is Static Device Binding supported? | Yes |
| --- | --- |

Networking Options

| • | Router, Clause 6 BACnet/IP (Annex J) to BACnet MS/TP |
| --- | --- |
|  | Annex H.3, BACnet Tunneling Router over UDP/IP |
| • | BACnet/IP Broadcast Management Device (BBMD) |
| Yes | Does the BBMD support registrations by Foreign Devices? |

Character Sets

| • | ANSI X3.4 |
| --- | --- |
|  | ISO 10646 (USC-2) |
|  | IBM™/Microsoft™ DBCS |
|  | ISO 10646 (ICS-4) |
|  | ISO 8859-1 |
|  | JIS C 6226 |